Pursuant to the authority vested in the Commissioner of Health by sections 201(1) and 225 of the Public Health Law, Subpart 5-1 of the State Sanitary Code, as contained in Chapter I of Title 10 of the Official Compilation of Codes, Rules and Regulations of the State of New York is amended as follows:

Section

GENERAL PROVISIONS

5-1.1	Definitions

SOURCES OF WATER SUPPLY

5-1.10 	Statement

5-1.11	Applicability

5-1.12 	Water quality for existing sources of water supply

5-1.13 	Sampling and analytical requirements

5-1.14 	Water quality for proposed sources of water supply

5-1.15 	Limitation

PLANNING, SITING, TREATMENT AND APPROVAL

5-1.20 	Applicability

5-1.21 	Siting requirements

5-1.22 	Approval of plans and completed works

5-1.23 	Reporting emergencies

5-1.24 	Approval of fluoridation of public water systems

5-1.25 	Disinfection of facilities

5-1.26 	Dewatering trenches

5-1.27 	Adequacy of distribution system

5-1.28 	Blowoff facilities

5-1.29 	Pumping equipment

5-1.30 	Providing treatment for public water systems

5-1.31 	Cross-connection control

5-1.32 	Protection of equalizing and distribution reservoirs

5-1.33 	Water supply emergency plans

CONTROL OF COPPER AND LEAD IN DRINKING WATER

5-1.40 	Applicability

5-1.41 	Lead and copper action levels

5-1.42 	Monitoring requirements for lead and copper in drinking water

5-1.43 	Monitoring requirements for water quality parameters

5-1.44 	Public education and supplemental monitoring requirements

5-1.45 	Corrosion control studies

5-1.46 	Corrosion control treatment

5-1.47 	Source water monitoring and treatment

5-1.48 	Lead service line replacement

5-1.49 	Reporting and record keeping requirements

PUBLIC WATER SYSTEMS; MAXIMUM CONTAMINANT LEVELS;

MONITORING REQUIREMENTS; NOTIFICATIONS REQUIRED

5-1.50 	Applicability and responsibility

5-1.51 	Maximum contaminant levels, maximum residual disinfectant levels and treatment technique requirements

5-1.52 	Tables

MONITORING AND CONTROL OF DISINFECTION BYPRODUCT PRECURSORS

5-1.60	Applicability

5-1.61	Monitoring requirement for disinfection byproduct precursors

5-1.62	Alternative compliance criteria for enhanced coagulation

5-1.63	Enhanced coagulation performance requirements

OPERATION AND QUALITY CONTROL

5-1.70 	Applicability

5-1.71 	Protection and supervision of public water systems

5-1.72 	Operation of a public water system

5-1.73 	Water treatment plant laboratory

5-1.74 	Approved laboratories

5-1.75 	Additional sampling requirements

5-1.76 	Monitoring of consecutive public water systems

5-1.77 	[Public health hazard] State notification

5-1.78 	[Content of consumer and public notifications] Public notification

5-1.79 	Multiple distribution systems

VARIANCES AND EXEMPTIONS

5-1.90 	Variance from a maximum contaminant level

5-1.91 	Variance from required use of any specified treatment technique

5-1.92 	Exemption from a maximum contaminant level or any treatment technique requirement

5-1.93 	Variance or exemption requests

5-1.94 	Notice and opportunity for public hearing

5-1.95 	Reserved

    - Enforceability of final schedule prescribed pursuant to granting of variance or exemption

SEPARABILITY

5-1.100 	Separability

APPENDICES

5-A	Recommended Standards for Water Works, 1997 Edition

5-B	Rural Water Supply, 1995 Edition

5-C	Acceptable Methods for the Analysis of Contaminants in Water

SUBPART 5-1

PUBLIC WATER SYSTEMS

GENERAL PROVISIONS

Section 5-1.1 is amended to read as follows:

Section 5-1.1 Definitions. As used in this Subpart the following words and terms shall have the stated meaning, except as otherwise specifically provided:

- Action level means the concentration of copper or lead that when exceeded triggers actions to be taken by a water system.

##### Copper action level = 1.3 milligrams per liter

Lead action level = 0.015 milligrams per liter

- Auxiliary source means a source of water supply which is not normally used but which has been approved for use by the department or other State agencies having jurisdiction, and has been developed for use when the normal source or sources fail to meet the water supply requirements.

- Coagulation means a process using coagulants and mixing by which colloidal and suspended material are destabilized and agglomerated into flocs.

- Commissioner means the Commissioner of Health of the State of New York.

- Community water system (CWS) means a public water system which serves at least five service connections used by year-round residents or regularly serves at least 25 year-round residents.

(f)	Comprehensive Performance Evaluation (CPE) is a thorough review and analysis of a treatment plant’s performance-based capabilities and associated administrative, operation and maintenance practices.  For purposes of compliance with section 5-1.72 (c) (2) (iv) of this Subpart, the CPE must consist of at least the following components: assessment of plant performance; evaluation of major unit processes; identification and prioritization of performance limiting factors; assessment of the applicability of comprehensive technical assistance; and preparation of a CPE report.

[Consumer notification means notification of all persons served by the system as follows:

(1)  Notification must be made, within 45 days of an MCL violation, of a failure to comply with a prescribed treatment technique, and/or of a failure to meet requirements of a variance or exemption schedule, either by mail delivery through a separate mailing or with the water bill or by hand delivery. The State may waive mail or hand delivery, if the State determines the system has corrected the violation or failure within the  45 day period. The State must grant or deny the waiver in writing within the 45 day period.

(2)  Following the initial public notification, notification must be made, at least every three months, of the failure to meet monitoring requirements, of the failure to use applicable testing procedure and/or of the granting of a variance or exemption, either by mail delivery through a separate mailing or with the water bill or by hand delivery.  The State may waive mail or hand delivery, if the system has corrected the violation or failure within the three-month period. The State must grant or deny the waiver in writing within the three-month period.

(3)  Notification shall be repeated at least once every three months if the violation or the failure to comply continues or the variance or exemption remains in effect.

(4)  The supplier of water shall provide the State with a copy of the notice.]

(g)	Contaminant means any physical, chemical, microbiological or radiological substance or matter in water.

(h)	Conventional filtration means a series of processes including coagulation, flocculation, sedimentation and filtration.

(i)	Corrosion inhibitor means a substance capable of reducing the corrosivity of water toward metal plumbing materials, especially lead and copper, by forming a protective coating on the interior surface of these materials.

(j)	CT means the product of the free residual disinfectant concentration (C) in milligrams per liter determined before or at the first customer, and the corresponding disinfectant contact time (T)  in minutes, expressed by the formula (C)  x (T)  = CT. Disinfectant contact time (T), is the time that it takes for water to move from the point of disinfectant application or the previous point of residual disinfectant measurement to a point before or at the point where residual disinfectant concentration (C)  is measured.

(k)	Designated representative means the health commissioner or health officer of a city of 50,000 population or over, or the health commissioner or health officer of a county or part-county health district, the state regional health director, or district director having jurisdiction; a public health director or public health engineer qualified as duly appointed pursuant to Part 11 of this Title; or a county health commissioner, or county health director having the powers and duties prescribed in section 352 of the Public Health Law, or any other individual so designated by the commissioner.

(l)	Disinfection station means a facility consisting of one or more points where water is routinely treated with an oxidant for disinfection, odor control or other purposes including the inactivation of pathogenic organisms and excluding treatment on a raw water transmission main.

(m) 	Distribution point means a sampling point representative of drinking water within the distribution system.

(n)	Department means the New York State Department of Health.

(o)	Diatomaceous earth filtration means a process resulting in substantial particulate removal which a precoat cake of diatomaceous earth filter media is deposited on a support membrane (septum), and while the water is filtered by passing through the cake on the septum, additional filter media known as body feed is continuously added to the feed water to maintain the permeability of the filter cake.

(p)	Direct filtration means a series of processes including coagulation and filtration but excluding sedimentation resulting in substantial particulate removal.

(q) 	Dose equivalent means the product of the absorbed dose from ionizing radiation and such factors as account for differences in biological effectiveness because of the type of radiation and its distribution in the body as specified by the International Commission on Radiological Units and Measurements (ICRU).

(r)	Dwelling unit means one or more rooms with provisions for living, sanitary and sleeping facilities arranged for the use of one family.

(s)	Effective corrosion inhibitor residual means a concentration sufficient to form a protective coating on the interior walls of a pipe.

(t)	Emergency source means a source of water supply which is not the regular source or auxiliary source and which is developed during an emergency for temporary use.

(u)	Enhanced coagulation means the addition of sufficient coagulant for improved removal of disinfection byproduct precursors by conventional filtration treatment.

([u]v)	Entry point means a representative sampling location after the last point of treatment but before the first consumer connection.

(w)	Filter profile is a graphical representation of individual filter performance, based on continuous turbidity measurements or total particle counts versus time for an entire filter run, from startup to backwash, that includes an assessment of filter performance while another filter is being backwashed.

([v]x)	Filtration means a process for removing particulate matter from water by passage through porous material.

([w]y)	First draw tap sample for lead and copper means a one liter sample of water collected from a cold water tap after the water has stood in the plumbing system for at least six hours and is collected without flushing the tap.

([x]z)	Flocculation means a process to enhance agglomeration or collection of smaller floc particles into larger, more easily settleable particles through gentle stirring by hydraulic or mechanical mechanisms.

(aa)	GAC10 means granular activated carbon filter beds with an empty-bed contact time of 10 minutes based on average daily flow and a carbon reactivation or replacement frequency of every 180 days, and is the Best Available Technology for compliance with total trihalomethanes (TTHM) and haloacetic acids (five) (HAA5) maximum contaminant levels (MCLs).

([y]ab)	Gross alpha particle activity means the total radioactivity because of alpha particle emission as inferred from measurements on a dry sample.

([z]ac)	Gross beta particle activity means the total radioactivity because of beta particle emission as inferred from measurements on a dry sample.

([aa]ad)Ground water directly influenced by surface water means any water beneath the surface of the ground which exhibits significant and rapid shifts in water characteristics such as turbidity, temperature, conductivity or pH which closely correlates to climatological or surface water conditions and/or which contains macroorganisms, algae, large diameter (three microns or greater) pathogens or insect parts of a surface water origin.

([ab]ae)Ground water source means a source of water supply taken from a ground water aquifer and developed in accordance with section 5-1.22 of this Subpart, but shall not include an admixture of surface water or water exposed to the ground surface.

(af)	Haloacetic acids (five) (HAA5) mean the sum of the concentrations in milligrams per liter of five specific haloacetic acid compounds, rounded to two significant figures after addition.  The five haloacetic acids that comprise the HAA5 are monochloroacetic acid, dichloroacetic acid, trichloroacetic acid, monobromoacetic acid, and dibromoacetic acid.

([ac]ag)Large water system means a water system that serves more than 50,000 persons.

([ad]ah)Lead service line means a service line made of lead which connects the water main to the building inlet and any lead appurtenances connected to the lead service line.

([ae]ai)Lead service line sample means a one liter sample for lead, collected after the water has stood in the service line for at least six hours. The sample must be collected directly from a tap on the service line or by calculating and wasting the amount of water in the plumbing system from the sampling point to the service line. At a single family structure, the sample may be collected by running the water until there is a significant change in water temperature.

([af]aj)	Man-made beta particle and photon emitters means all radionuclides emitting beta particles and/or photons, except the daughter products of thorium-232, uranium-235 and uranium-238, listed in Maximum Permissible Body Burdens and Maximum Permissible Concentration of Radionuclides in Air or Water for Occupational Exposure, National Bureau of Standards, Handbook 69, as amended August 1963, U.S. Department of Commerce. Copies of this publication are available from N.C.R.P. Publications, 7910 Woodmont Avenue, Bethesda, MD, and a copy is available for inspection and copying at the offices of the records access officer of the Department of Health, Corning Tower, Empire State Plaza, Albany, NY 12237.

([ag]ak)Maximum contaminant level (MCL) means the maximum permissible level of a contaminant in water, which is delivered to any user of a public water system.  For entry point turbidity and inorganic chemicals listed in section [5-1.51] 5-1.52 tables 1 and 2 of this Subpart, the maximum permissible level is measured at the point of entry to the distribution system.  For  organic chemicals with MCLs listed in section 5-1.52 table 3 of this Subpart, the MCL is measured at the individual sources, unless otherwise specified by the State.  Substances added to the water by the user, and limited to the premises of the user, are excluded from this definition.

(al)	Maximum residual disinfectant level (MRDL) means a level of disinfectant measured at a consumer’s tap, above which the possibility of unacceptable health effects exists.

([ah]am)Maximum total trihalomethane potential (MTP) means the maximum concentration of total trihalomethane produced in a given water containing a free chlorine residual after seven days at a temperature of 25 degrees Celsius or above.

([ai]an)	Medium water system means a water system that serves greater than 3,300 and less than or equal to 50,000 persons.

([aj]ao)	Noncommunity water system (NCWS) means a public water system that is not a community water system.

([ak]ap)Nontransient noncommunity water system (NTNC) means a public water system that is not a community water system but is a subset of a noncommunity water system that regularly serves at least 25 of the same [persons] people, four hours or more per day, for four or more days per week, for 26 or more weeks per year.

([al]aq)	Optimal corrosion control treatment means the corrosion control treatment that reduces the lead and copper concentrations at users' taps to the lowest reasonably achievable level while insuring that the treatment does not cause the water system to violate Part 5 of the State Sanitary Code or cause adverse health or operational effects.

([am]ar)Person means an individual, corporation, company, association, partnership, State agency, municipality, including a county, or Federal agency.

([an]as)Picocurie means that quantity of radioactive material producing 2.22 nuclear transformations per minute.

([ao]at)	Potable water means a water which meets the requirements established by this Subpart.

([ap]au)Point of use means the free-flowing outlet of the ultimate user of a public water system.

([aq]av)Principal organic contaminant (POC) means any organic chemical compound belonging to the following classes, except for trichloromethane (chloroform), dibromochloromethane, bromodichloromethane, tribromomethane (bromoform) and any other organic contaminant with a specific MCL listed in section [5.1-52] 5-1.52 table 3 of this Subpart[;]:

- Halogenated alkane: Compound containing carbon (C), hydrogen (H) and halogen (X) where X = fluorine (F), chlorine (Cl), bromine (Br) and/or iodine (I), having the general formula CnHyXz, where y + z = 2n + 2; n, y and z are integer variables; n and z are equal to or greater than one and y is equal to or greater than zero[.];

- Halogenated ether: Compound containing carbon (C), hydrogen (H), oxygen (O) and halogen X (where X = F, Cl, Br and/or I) having the general formula CnHyXzO, where y + z = 2n + 2; the oxygen is bonded to two carbons; n, y and z are integer variables; n is equal to or greater than two, y is equal to or greater than zero and z is equal to or greater than one[.];

- Halobenzenes and substituted halobenzenes:  Derivatives of benzene which have at least one halogen atom attached to the ring and which may or may not have straight or branched chain hydrocarbon, nitrogen or oxygen substituents[.];

- Benzene and alkyl- or nitrogen-substituted benzenes:  Benzene or a derivative of benzene which has either an alkyl- and/or a nitrogen-substituent[.];

- Substituted, unsaturated hydrocarbons: A straight or branched chain unsaturated hydrocarbon compound containing one of the following:  halogen, aldehyde, nitrile, amide[.]; and

- Halogenated non-aromatic cyclic hydrocarbons:  A non-aromatic cyclic compound containing a halogen.

([ar]aw)Public health hazard means an existing or imminent condition which can be responsible for or cause illness, injury or death and for which immediate corrective or remedial action is required. Public health hazards include, but are not limited to, the following:

- [Four or more monthly MCL violations for total coliform in any twelve month period for a public water system on a monthly monitoring schedule  or two or more quarterly MCL violations for total coliform in any twelve month period for a public water system on a quarterly monitoring schedule or any Escherichia coli (E. coli) MCL violation and/or primary inorganic chemical, organic chemical or radiological MCL violations in  two consecutive monitoring periods and/or a nitrate violation;] an Escherichia coli (E. coli) MCL violation, or failure to test for E. coli after any repeat sample tests positive for coliform;

(2)	a nitrate/nitrite MCL violation, or failure to take a confirmation sample within 24 hours for nitrate or nitrite after an initial sample exceeds the MCL;

(3)	an acute MRDL violation for chlorine dioxide as specified in section 5-1.52 table 3A of this Subpart, or failure to take the required samples in the distribution system the day after the MRDL is exceeded at the entry point as specified in section 5-1.52 table 15A of this Subpart;

(4)	turbidity violations or exceedances specified in paragraph 5-1.78(d)(3) of this Subpart and determined by the State to present an existing or imminent condition which can be responsible for or cause illness, injury or death and for which immediate corrective or remedial action is required;

([2]5)	use of an unapproved or contaminated water supply source;

([3]6)	insufficient quantity of water to meet drinking or sanitary demands;

([4]7)	hazardous or toxic chemical contamination;

([5]8)	disinfection which is inadequate to destroy harmful microorganisms  or to maintain a specified chlorine residual;

([6]9)	disruption of water service of four hours or more, determined by the State to present an existing or imminent condition which can be responsible for or cause illness, injury or death and for which immediate corrective or remedial action is required;

([7]10)	cross-connections of sufficient hazard to adversely affect the health of a water consumer; and

([8]11)	any other conditions, including a waterborne disease outbreak,  determined to be a public health hazard by the commissioner.

([as]ax)Public notification means disseminating information about a problem with a public water system in a form and manner consistent with section 5-1.78 of this Subpart.  [in a manner and format commensurate with the degree of severity of the cause of said notification which can reasonably be expected to make the public aware of the contents of the notice. The notification must be made in the following manner:

- Publication in a newspaper of general circulation in the area served by the water system within 14 days after the supplier of water learns of a failure to comply. For a public health hazard, publication must be made within 48 hours of learning of the determination of a public health hazard.

(i)	If there is no daily newspaper of general circulation in the area served by the water system, publish for at least three consecutive weeks, in a weekly newspaper of general circulation. The first publication shall be made within 14 days of learning of the failure to comply.

(ii)	If there is no daily or weekly newspaper of general circulation in the area served by the system or if notification can not be published within 14 days after the supplier of water learns of a failure to comply or within 48 hours of learning of the determination of a public health hazard, hand deliver to all consumers or post in conspicuous places in area served by the system within 14 days after the supplier of water learns of a failure to comply or within 48 hours of learning of the determination of a public health hazard. Notice by hand delivery must be repeated, at least every three months, if the failure to comply or the public health hazard continues. Notice by posting must be continued if the failure to comply or the public health hazard continues.

- Providing a notice to the radio and television stations serving the area served by the water system within 48 hours after the supplier of water learns of the determination of a public health hazard.

- The supplier of water shall provide the State with copies of the notification made to the newspaper and to the radio and television stations before making the required notification but no later than 10 days of learning of the failure to comply.

- Where necessary, based on census information, as determined by the State, notification shall be multilingual.]

([at]ay)  Public water system means a community, noncommunity or nontransient noncommunity water system which provides water to the public for human consumption through pipes or other constructed conveyances, if such system has at least five service connections or regularly serves an average of at least 25 individuals daily at least 60 days out of the year.  Such term includes:

- collection, treatment, storage and distribution facilities under control of the supplier of water of such system and used with such system; and

- collection or pretreatment storage facilities not under such control which are used with such system.

([au]az) Raw water means water immediately before the first or only point of disinfection or other treatment.

([av]ba) Regular source means a source of water supply which is normally used and is approved by the department and other State agencies having jurisdiction.

([aw]bb) Rem means the unit dose equivalent from ionizing radiation to the total body or any internal organ or organ system.

([ax]bc) Millirem (MREM) means 0.001 of a rem.

([ay]bd) Reporting period means a time period designated by the State for determining maximum contaminant level compliance.

([az]be) Sedimentation means a process for removal of solids before filtration by gravity or separation.

([ba]bf)  Service connection means the pertinent pipes, valves and fittings that connect a distribution system to a consumer's facility.

([bb]bg)  Single family structure means a building constructed as a single-family residence that is currently used as either a residence or a place of business.

([bc]bh)  Slow sand filtration means a process involving passage of raw water through a bed of sand at low velocity resulting in particulate removal by physical or biological mechanisms.

([bd]bi) Small water system means a water system that serves 3,300 or fewer persons.

([be]bj)  Source of water supply means any ground water aquifer, surface water body or watercourse from which water is taken either periodically or continuously for drinking, culinary or food-processing purposes, or which has been designated for present or future use as a source of water supply for domestic or municipal purposes.

([bf]bk) State means the State Commissioner of Health, or his designated representative.

([bg]bl) State notification means notifying the State by telephone, facsimile (FAX) copy, e-mail or other means about [within 24 hours of learning of] the existence or potential existence of a public health hazard, or the existence of any other violation or situation that may pose a risk to public health [within 48 hours after the supplier of water learns of a failure to comply. The initial telephone notification to the State shall be confirmed, by the supplier of water within 24 hours, by certified letter].

([bh]bm)Supplier of water means any person who owns or operates a public water system.

([bi]bn)Surface water means all water open to the atmosphere and subject to surface runoff.

(bo)	SUVA means the UV absorption at 254 nanometers (measured in 1/meters) divided by the dissolved organic carbon concentration (measured in mg/L).  SUVA is an indicator of the humic content of water and the ability of the water to be treated for the removal of disinfection byproduct precursors.

(bp)	Tier 1 notification means the category for public notifications that are required within 24 hours of learning of a public health hazard.  Section 5-1.78(c) of this Subpart lists the specific requirements for Tier 1 notifications.

(bq)	Tier 2 notification means the category for public notifications that are required within 30 days of learning of a violation or situation with the potential to have serious adverse effects on human health after long term exposure, such as most MCL, MRDL and treatment technique violations that are not public health hazards.  Section 5-1.52 table 13 of this Subpart lists violations and situations that require Tier 2 notification; section 5-1.78(d) of this Subpart lists the specific requirements for Tier 2 notifications.

(br)	Tier 3 notification means the category for public notifications that are required within one year (30 days for transient noncommunity water systems) of learning of a less serious violation or situation that does not require a Tier 1 or Tier 2 notification, such as most monitoring violations.  Section 5-1.52 table 13 of this Subpart lists violations and situations that require Tier 3 notification; section 5-1.78(e) of this Subpart lists the specific requirements for Tier 3 notifications.

(bs)	Total Organic Carbon (TOC) means total organic carbon in mg/L, measured by converting organic carbon to carbon dioxide, rounded to two significant figures.

([bj]bt)	Total trihalomethane (TTHM) means the sum of the concentration of trichloromethane (chloroform), dibromochloromethane, bromodichloromethane and tribromomethane (bromoform).

(bu)	Transient noncommunity water system (TNC) means a noncommunity water system that does not regularly serve at least 25 of the same people over six months per year.

([bk]bv)Unspecified organic contaminant (UOC) means any organic chemical compound not otherwise specified in this Subpart.

([bl]bw)Virus means a virus of fecal origin, which is infectious to humans by waterborne transmission.

([bm]bx)Violation means failure to comply with or conform to the provisions of this Subpart.

([bn]by)Waterborne disease outbreak means the occurrence of acute infectious illness epidemiologically associated with the ingestion of water from a public water system.

([bo]bz)Watercourse means any surface water listed in 6 NYCRR, Chapter 10.

([bp]ca)Water supply emergency plan means a plan approved by the State and filed with the State at such location as specified by the commissioner. The plan shall address the actions to be taken by a water supplier to anticipate water supply emergencies and the steps to be taken to ensure the delivery of potable water during a water supply emergency.

([bq]cb)Water treatment plant means any plant or equipment which, through the addition of chemicals or through aeration, ion exchange, demineralization, coagulation, sedimentation or filtration, or through any other means or combinations of treatment, shall change the physical, chemical, radiological or microbiological quality of water.

Subdivision (a) of Section 5-1.12 is amended to read as follows:

- Whenever the supplier of water determines or is advised by the State that one or more of the MCLs set forth in this Subpart are or may be exceeded; or that effectiveness of treatment processes diminishes to the extent that a violation of the treatment techniques or MCLs set forth in this Subpart may occur; or that any deleterious changes in raw water quality have occurred; or that a change in the character of the watershed or aquifer has been observed which may affect water quality; or that any combination of the preceding exists, the supplier of water shall notify the State and do the following:

- undertake a study to determine the cause or causes of such conditions, independent of known or anticipated treatment technology;

- modify existing or install treatment to comply, to the extent practicable, with sections 5-1.30, 5-1.50, [and] 5-1.51 and 5-1.60 of this Subpart;

- initiate water sampling as needed to delineate the extent and nature of the cause of concern;

- investigate all or part of the watershed or aquifer to verify any existing or potential changes in the character of the sources of water supply; and

- submit a written report to the State within 30 days of the onset of the foregoing conditions summarizing the findings outlined in paragraphs (1) through (4) of this subdivision.

Subdivisions (b), (c) and (d) of Section 5-1.30 are amended to read as follows:

(b)	Minimum treatment for surface water sources or ground water sources directly influenced by surface water shall be filtration and disinfection techniques, approved by the State in accordance with section 5-1.22 of this Subpart, capable of 99 percent removal of Cryptosporidium oocysts, 99.9 percent removal and/or inactivation of Giardia lamblia cysts and 99.99 percent removal and/or inactivation of viruses, between a point where the raw water is no longer subject to recontamination by surface water runoff and a point downstream before or at the first consumer. Compliance with this treatment technique requirement shall be no later than June 29, 1993 for surface water sources or within 18 months for ground water sources determined to be directly influenced by surface water sources, unless the department determines that the supplier of water can meet specific avoidance criteria as defined in subdivision (c)  of this section. Required performance monitoring shall be conducted in accordance with section 5-1.52 table 10A of this Subpart.  Compliance with these treatment technique requirements shall also include:

- filtration facilities designed and operated to meet performance standards in accordance with section 5-1.52 table 4A of this Subpart;

- for systems using chlorine, the free chlorine residual disinfection concentration in the water entering the distribution system can not be less than 0.2 milligrams per liter for more than four hours.  Continuous monitoring is required, except as provided in section 5-1.52 table 15 of this Subpart.

(3)	By June 8, 2004, any system that recycles spent filter backwash water, thickener supernatant, or liquids from dewatering process must return these flows through the processes of a system's existing conventional or direct filtration system.

(c)	A public water system that uses a surface water source or a ground water source directly influenced by surface water which fails to comply with any of the following avoidance criteria shall develop and submit to the State, within three months [or by March 31, 1992 whichever is later] of such failure to comply, a written plan for installing filtration and disinfection. Also, filtration and disinfection shall be installed, in accordance with subdivision (b)  of this section, within 18 months[or by June 29, 1993, whichever is later] of such failure to comply .

- Raw water fecal coliform concentrations must be equal to or less than 20 colonies per 100 milliliters or total coliform concentration must be equal to or less than 100 colonies per 100 milliliters in at least 90 percent of measurements made over the previous six months that the system was in operation.  Monitoring shall be conducted in accordance with section 5-1.52 table 11A of this Subpart. If both fecal and total coliform analyses are performed, the fecal coliform results will take precedence.

- Raw water turbidity levels must not exceed five nephelometric turbidity units unless the department determines that the turbidity was caused by an unusual and unpredictable event. No more than two such events in the previous 12 months or no more than five events in the previous 120 months that the system was in operation are allowed.  An event means a series of consecutive days during which at least one turbidity measurement each day exceeds five nephelometric turbidity units. Monitoring is to be conducted in accordance with section 5-1.52 Table 10A of this Subpart.

- Disinfection must be sufficient to ensure at least 99.9 percent inactivation of Giardia lamblia cysts and 99.99 percent inactivation of viruses, between a point where the raw water is no longer subject to recontamination by surface water runoff and a point downstream before or at the first consumer.  Actual CT values must be equal to or greater than the required values found in section 5-1.52 tables 14A through 14G of this Subpart, except for one day in each month that the system served water to the public, or except where the State determines that an additional failure in one month in the previous twelve months was caused by circumstances that were unusual and unpredictable. The supplier of water must calculate the CT values of the system for each day the system is in operation to document satisfactory disinfection. The necessary parameters and related monitoring frequencies to conduct this evaluation include:

- temperature of the disinfected water measured at least once per day at each residual disinfectant concentration sampling point;

- pH of the disinfected water, measured at least once per day at each chlorine residual disinfectant concentration sampling point by systems using chlorine;

- the disinfectant contact time (T), determined daily during peak hourly flow; and

- the residual disinfectant concentration (C), before or at the first customer, measured daily during peak hourly flow.

- The disinfection system must have redundant components to ensure continuous disinfection. Auxiliary power with automatic start and alarm is required at all disinfection facilities where a power outage would result in a loss or reduction in the ability of the system to maintain a disinfection concentration as required by this Subpart.

- For systems using chlorine, the free chlorine residual disinfection concentration in the water entering the distribution system cannot be less than 0.2 milligrams per liter for more than four hours, unless the State determines that any such failure was caused by circumstances that were unusual and unpredictable. Continuous monitoring is required except as provided in section 5-1.52 table 15 of this Subpart.

- The disinfection residuals or the heterotrophic plate count results in the water in the distribution system must meet the requirements outlined in subdivision (g) of this section and section 5-1.52 Table 11 of this Subpart  unless the State determines that the failure to meet the requirements was not caused by a deficiency in the treatment of the source water.

- The watershed control program must provide natural or man made barriers to the occurrence, transport and/or survival of Cryptosporidium oocysts, Giardia lamblia cysts and viruses.  The watershed control program must include, but is not limited to the following:

- ownership or protective controls of the watershed, except where the supplier of water submits written justification to show that the travel time of the water to the intake is greater than 60 days under all but emergency conditions. Protective controls can include written agreements with landowners within the watershed but must include as a minimum the absence of any bathing beach as defined in Part 6-2 of this Title, except for a bathing beach owned and/or maintained by an individual for use by the individual's family or friends;

- no new sewage discharges to any watercourse shall be allowed where the time of travel from the point of discharge to the intake is 60 days or less. Existing sewage discharges with a current State Pollutant Discharge Elimination System (SPDES)  permit issued by the New York State Department of Environmental Conservation, where the time of travel from the point of discharge to the intake is 60 days or less, shall, as a minimum, have secondary treatment followed by sand filtration and disinfection at facilities designed to achieve 99.9 percent removal and/or inactivation of Giardia lamblia cysts and 99.99 percent removal and/or inactivation of viruses by June 29, 1993.  Existing or new sewage discharges with a SPDES permit issued by the New York State Department of Environmental Conservation, where the time of travel from the point of discharge to the intake is greater than 60 days, shall, as a minimum, have secondary treatment followed by sand filtration and disinfection at facilities designed to achieve 99.9 percent removal and/or inactivation of Giardia lamblia cysts and 99.99 percent removal and/or inactivation of viruses by June 29, 1993 or a later date set forth in a plan submitted to the commissioner and approved using the criteria for the long term plan as described in section 5-1.30(c)(7)(vii)  of this Subpart. The sewage treatment facilities required herein shall be operated in conformance with their design specifications and the conditions of their SPDES permit.

- watershed rules and regulations promulgated and enforced in accordance with Title I of Article 11 of the Public Health Law; including as a minimum prohibition or controls on waste discharges which contain or potentially may contain Cryptosporidium oocysts, Giardia lamblia cysts, and/or viruses;

- identification and evaluation of pertinent geological, hydrological and physical characteristics or features and potential conditions or activities which may influence  water quality;

- a monitoring and surveillance program to assess water quality and water quantity trends;

- an annual report submitted by the supplier of water to the department describing watershed activities, especially activities that affect water quality, identifying new and existing water quality concerns and remediation efforts taken and any other reports required pursuant to adopted watershed rules and regulations. The annual report must be submitted to the department no later than the 10th of October of each year; and

- a long term plan for the implementation of the watershed control program, including a description of the commitment of human and financial resources for such program shall be submitted to the commissioner for approval from systems that serve more than 100,000 persons, obtain water from a watershed or watersheds that involve multiple political subdivisions and own less than 25 percent of the land in the watershed. The approval shall be based on the exercise of a reasonable discretion by the commissioner in reviewing and accepting the proposed levels of human and fiscal resources to be committed for successful implementation of the plan, measured by projected cost of the administration, inspection, enforcement, land acquisition, sewage treatment plant upgrading and other activities and/or services related to such watershed control program, including the resolution of inherent water quality and quantity questions and the reliability of the method of funding. Failure to obtain the approval of the long term plan or failure to secure the required human or financial resources will result in a requirement to provide filtration, in accordance with the provisions of this Subpart.  The approval of the long term plan shall be for a period of ten years, subject to further review and approval for successive ten year periods. Notwithstanding any approval granted pursuant hereto, if Federal or State law or regulation shallhenceforth unconditionally mandate filtration of surface water sources, then any such approvals shall forthwith cease and terminate with filtration thereafter to be provided, in accordance with the provisions of this Subpart, when reasonably feasible.

- The public water system must not have been identified as a source of a waterborne disease outbreak since 1980.

- The public water system must comply with the trihalomethane, haloacetic acid, bromate, and chlorite maximum contaminant levels and the maximum residual disinfectant levels in accordance with section 5-1.52 of this Subpart.

- The public water system must comply with the maximum contaminant level for total coliform in accordance with section 5-1.52 of this Subpart in eleven months of the twelve previous months that the system served water to the public on an ongoing basis, unless the State determines that failure to meet this requirement was not caused by a deficiency in treatment of the source water.

- Notwithstanding anything to the contrary in sections 5-1.12, 5-1.23, 5-1.51[, 5-1.52 table 13] or 5-1.77 of this Subpart, if the public water system fails to comply with the treatment technique and/or the monitoring requirements of subdivisions (b), (c) or (g) of this section, fails to install the filtration and/or disinfection treatment facilities required by this section or fails to comply with the avoidance criteria requirements contained in subdivision (c) of this section, the system violates this Subpart and shall make State[, consumer] and public notification, including any required mandatory health effects language.  Pursuant to subdivision[s 5-1.30(b) ] (c) of this section, if at any time the raw water turbidity exceeds five nephelometric turbidity units, the system shall consult with the State within 24 hours of learning of the exceedance.  Based on this consultation, the State may determine that the exceedance constitutes a public health hazard, as defined in paragraph 5-1.1(aw)(4) of this Subpart, which requires a Tier 1 notification. When consultation does not take place within the 24 hour period, the water system must distribute a Tier 1 notification no later than 48 hours after the system learns of the violation. [make State, consumer and public notification.] Pursuant to subdivisions (b) and (c) of this section, if the free chlorine residual falls below 0.2 milligrams per liter in the water entering the distribution system, for a system using chlorine, the system shall make State notification. The system must make State notification whether the residual was restored to at least 0.2 milligrams per liter within four hours.

Section 5-1.51 is amended to read as follows:

5-1.51 Maximum contaminant levels, maximum residual disinfectant levels and treatment technique requirements.

- The maximum contaminant levels, maximum residual disinfectant levels and treatment technique requirements are listed in section 5-1.52 tables 1 through 7 of this Subpart.  In the case where an MCL, MRDL, or treatment technique requirement is exceeded, notwithstanding anything to the contrary contained in section 5-1.12 of this Subpart, the supplier of water will take the necessary steps to comply with this section, to ensure the protection of the public health, including the undertaking of remedial feasibility studies and the installation of a suitable treatment process. Compliance with the MCLs, MRDLs and treatment technique requirements shall be determined by the procedures contained in section 5-1.52 tables 1 through 7 of this Subpart.

- The minimum monitoring requirements for each contaminant are listed in section 5-1.52 tables 8A through 12 and 15A of this Subpart, except for public water systems with fewer than 15 service connections and which serve fewer than 25 persons, where monitoring will be at State discretion. For this section, State discretion shall mean requiring monitoring when the State has reason to believe an MCL, MRDL, or treatment technique requirement has been violated, the potential exists for an MCL, MRDL, or treatment technique violation or a contaminant may present a risk to public health.

(c)	Each system required to monitor for disinfection byproducts must develop and implement a monitoring plan.  The system must maintain the plan and make it available for inspection by the State and the general public no later than 30 days after the compliance date.  If the system is a community or nontransient noncommunity system that uses surface water or ground water under the direct influence of surface water and serves 10,000 or more people, the monitoring plan must be made available by January 31, 2002.  If the system is a community or nontransient noncommunity system that uses surface water or ground water under the direct influence of surface water and serves fewer than 10,000 people, or it is a community or nontransient noncommunity system using only ground water, the monitoring plan must be made available by January 31, 2004.  All community and nontransient noncommunity systems using surface water or ground water under the direct influence of surface water that serve more than 3,300 people must submit a copy of the monitoring plan to the State, or provide written acknowledgement and acceptance of a plan provided by the State, no later than the date of the first report required in section 5-1.72 of this Subpart. After review, the State may require changes in any plan elements.  Failure to monitor in accordance with the monitoring plan is a monitoring violation.  Systems may use only data collected in accordance with the monitoring plan to qualify for reduced monitoring of disinfection byproducts or disinfection byproduct precursors.  The monitoring plan must include at least the following elements, as applicable:

(1)	specific locations and schedules for collecting samples for any parameters listed in this section;

(2)	how the system will calculate compliance with MCLs, MRDLs, and treatment techniques;

(3)	if approved for monitoring as a consecutive system, or if providing water to a consecutive system, under the provisions of section 5-1.76 of this Subpart, the sampling plan must reflect the entire distribution system.

([c]d)	The notification requirements for each contaminant are listed in section 5-1.52 table 13 of this Subpart.

([d]e)	The CT values for inactivation of Giardia lamblia cysts by free chlorine at various pH and temperature levels are listed in section 5-1.52 tables 14A through 14F of this Subpart. The CT values for inactivation of Giardia lamblia cysts by chlorine dioxide and ozone at various temperature levels are listed in section 5-1.52 table 14G of this Subpart.

([e]f)	The alternative disinfection monitoring frequency requirements using grab samples instead of continuous chlorine concentration monitoring is listed in section 5-1.52 table 15 of this Subpart.

([f]g)	Monitoring and reporting frequencies for specific contaminants may be established at State discretion whenever the State believes that a potential exists for an MCL or MRDL violation or a [the] contaminant may present a risk to public health.

([g]h)	Notwithstanding anything to the contrary in subdivision (a) of this section, the Commissioner may recommend values lower than the MCLs if sufficient valid information based on commonly accepted scientific standards and principles demonstrates an increased public health concern.  Within one year from the date of such recommendation, the State shall hold a public hearing regarding the justification for the lower value, and whether a new MCL is warranted.

([h]i)	Notwithstanding anything to the contrary in section 5-1.52 table 3 the Commissioner may in specific cases except specific organic chemicals from the MCLs for general organic chemicals if the supplier of water can demonstrate that sufficient valid scientific information exists to show that the organic chemical does not pose an unreasonable risk to human health, the organic chemical is present at a level and under circumstances not indicative of contamination, and the cost of compliance is unreasonable in light of the risk to human health.

([i]j)	Notwithstanding anything to the contrary in section 5-1.52 table 3 of this Subpart, the Commissioner may, based on receipt and review of a justification submitted by the supplier of water, allow a higher MCL for a period of up to 60 days following application of a paint or lining to a potable water structure, if he determines that an unreasonable risk to human health does not exist.

- Notwithstanding anything to the contrary in section 5-1.52 table 3A of this Subpart, systems may increase residual disinfectant levels of chlorine or chloramines (but not chlorine dioxide) in the distribution system to a level and for a time necessary to protect public health, to address specific microbiological contamination problems caused by circumstances such as, but not limited to, distribution line breaks, storm run-off events, source water contamination events, or cross-connection events.

- A system that is installing granular activated carbon (GAC) or membrane technology to comply with the trihalomethane and haloacetic acid MCLs listed in section 5-1.52 table 3 may apply to the State for an extension of up to 24 months past the compliance dates for those MCLs.  Systems must comply with any interim measures and schedules of compliance set by the State.

([j]m)	Each public water system must certify annually in writing to the State that when Acrylamide and Epichlorohydrin are used in drinking water systems, the combination (or product) of dose and monomer level does not exceed the levels specified as follows:

Acrylamide = 0.05% dosed at 1 ppm (or equivalent)

Epichlorohydrin = 0.01% dosed at 20 ppm (or equivalent)

Certification can rely on manufacturers or third parties, as approved by the State.

([k]n)	For microbiological analysis, a standard sample size of 100 milliliters shall be used.

Section 5-1.52, Tables 1, 2, 3, 4A, 8B, 9A, 10A and 15 are amended as follows, Table 13 is repealed in its entirety and new Tables 3A, 13 and 15A are added as follows:

Table 1.  Inorganic Chemicals and Physical Characteristics

# Maximum Contaminant Level Determination

| Contaminants | MCL (mg/L)4 | Determination of MCL violation |
| --- | --- | --- |
| Asbestos | 7.0 million fibers/liter (MFL) (longer than 10 microns) | If the results of a monitoring sample analysis exceed the MCL, the supplier of water shall collect one more sample from the same sampling point within 2 weeks or as soon as practical. An MCL violation occurs when the average1 of the two results exceeds the MCL. |
| Antimony | 0.006 |  |
| Arsenic | 0.05 |  |
| Barium | 2.00 |  |
| Beryllium | 0.004 |  |
| Cadmium | 0.005 |  |
| Chromium | 0.10 |  |
| Cyanide (as free Cyanide) | 0.2 |  |
| Mercury | 0.002 |  |
| Selenium | 0.05 |  |
| Silver | 0.1 |  |
| Thallium | 0.002 |  |
| Fluoride | 2.2 |  |
| Chloride | 250.0 |  |
| Iron | 0.32 |  |
| Manganese | 0.32 |  |
| Sodium | No designated limits3 |  |
| Sulfate | 250.0 |  |
| Zinc | 5.0 |  |
| Color | 15 Units |  |
| Odor | 3 Units |  |
| Bromate5 | 0.010 | Compliance is based on a running annual average of monthly samples, computed quarterly. If the average of samples covering any consecutive four-quarter period exceeds the MCL, the system is in violation of the MCL and must notify the public. |
| Chlorite6 | 1.0 | Compliance is based on an average of each three-sample set taken in the distribution system in accordance with Table 8B. If the average exceeds the MCL, the system is in violation of the MCL and must notify the public. |

1Rounded to the same number of significant figures as the MCL for the contaminant in question.

2If iron and manganese are present, the total concentration of both should not exceed 0.5 mg/L.  Higher levels may be allowed by the State when justified by the

supplier of water.

3Water containing more than 20 mg/L of sodium should not be used for drinking by people on severely restricted sodium diets.  Water containing more than

270 mg/L of sodium should not be used for drinking by people on moderately restricted sodium diets.

4mg/L = milligrams per liter

5Community and nontransient noncommunity systems using ozone for disinfection or oxidation must comply with the bromate standard.  Systems using surface water or ground water under the direct influence of surface water and serving 10,000 or more people must comply by January 1, 2002.  Systems using surface water or ground water under the direct influence of surface water and serving fewer than 10,000 people, or systems using ground water must comply by January 1, 2004.

6Community and nontransient noncommunity systems using chlorine dioxide as a disinfectant or oxidant must comply with the chlorite standard.   Systems using surface water or ground water under the direct influence of surface water and serving 10,000 or more people must comply by January 1, 2002.  Systems using surface water or ground water under the direct influence of surface water and serving fewer than 10,000 people, or systems using ground water must comply by January 1, 2004.

Table 2 - Nitrate, Nitrite, Total Nitrate/Nitrite Maximum

# Contaminant Level Determination

| Contaminant | MCL (mg/L) | Determination of MCL violation |
| --- | --- | --- |
| Nitrate | 10 (as Nitrogen)1 | If the results of a monitoring sample analysis exceed the MCL, the supplier of water shall collect another sample from the same sampling point, within 24 hours of the receipt of results or as soon as practical.2 An MCL violation occurs when the average of the two results exceeds the MCL. |
| Nitrite | 1 (as Nitrogen) |  |
| Total Nitrate and Nitrite | 10 (as Nitrogen) |  |

1 An MCL of 20 mg/L may be permitted at a noncommunity water system if the supplier of water demonstrates that:

(a)  the water will not be available to children under six months of age;

(b)  a notice that nitrate levels exceed 10 mg/L and the potential health effects of exposure will be continuously posted [in conspicuous places in the area served by the system, within 14 days of the confirmation of an MCL violation] according to the requirements of a Tier 1 notification;

(c) the State will be notified annually of nitrate levels that exceed 10 mg/L; and

(d) no adverse health effects shall result.

2 Systems unable to collect an additional sample within 24 hours must issue a Tier 1 notification [public notice to consumers] and must collect the additional sample within two weeks of receiving the initial sample results.

Table 3. Organic Chemicals

Maximum Contaminant Level Determination

| Contaminants | MCL (mg/L) | Type of water system | Determination of MCL violation |
| --- | --- | --- | --- |
| General organic chemicals Principal organic contaminant (POC) Unspecified organic contaminant (UOC) Total POC’s and UOC’s | 0.005 0.05 0.1 | Community, NTNC and Noncommunity | If the results of a monitoring sample analysis exceed the MCL, the supplier of water shall collect one to three more samples from the same sampling point, as soon as practical, but within 30 days. An MCL violation occurs when at least one of the confirming samples is positive and the average of the initial sample and all confirming samples exceeds the MCL. |
| [Trihalomethanes] Disinfection Byproducts1,2 Total trihalomethanes Haloacetic acids | [0.1] 0.08 0.06 | Community and NTNC | The results of all analyses per quarter must be arithmetically averaged and must be reported to the State within 30 days of the public water system’s receipt of the analyses. A violation occurs if the average of the four most recent sets of quarterly samples (12-month running average) exceeds the MCL. If a system fails to complete four consecutive quarters of monitoring, compliance with the MCL will be based on an average of the available data. For systems monitoring less than quarterly, compliance must be based on an average of samples taken that year. If, during the first year of monitoring, any individual quarter’s average will cause the annual average of that system to exceed the MCL the system is out of compliance at the end of that quarter. |
|  |  | Transient Noncommunity | Not applicable. |

Table 3. Organic Chemicals

Maximum Contaminant Level Determination (continued)

| Contaminants | MCL (mg/L) | Type of water system | Determination of MCL violation |
| --- | --- | --- | --- |
| Specific Organic Chemicals Alachlor Aldicarb Aldicarb sulfone Aldicarb sulfoxide Atrazine Benzo(a)pyrene Carbofuran Chlordane Di(2-ethylhexyl)phthalate Dibromochloropropane (DBCP) 2,4-D Dinoseb Diquat Endrin Ethylene dibromide (EDB) Heptachlor Heptachlor epoxide Hexachlorobenzene Lindane Methoxychlor Pentachlorophenol Polychlorinated biphenyls (PCBs) Propylene glycol Simazine Toxaphene 2,4,5-TP (Silvex) 2,3,7,8-TCDD (dioxin) Vinyl chloride | 0.002 0.003 0.002 0.004 0.003 0.0002 0.04 0.002 0.006 0.0002 0.05 0.007 0.02 0.002 0.00005 0.0004 0.0002 0.001 0.0002 0.04 0.001 0.0005 1.0 0.004 0.003 0.01 0.00000003 0.002 | Community, NTNC and Noncommunity | If the results of a monitoring sample analysis exceed the MCL, the supplier of water shall collect one to three more samples from the same sampling point, as soon as practical, but within 30 days. An MCL violation occurs when at least one of the confirming samples is positive and the average of the initial sample and all confirming samples exceeds the MCL. |

1Systems using surface water or ground water under the direct influence of surface water and serving 10,000 or more people must comply with the disinfection byproducts standards by January 1, 2002.  Systems using surface water or ground water under the direct influence of surface water and serving fewer than 10,000 people, or systems using ground water must comply by January 1, 2004.  Until then, community water systems serving fewer than 10,000 persons must comply with an MCL of 0.1 mg/L for total trihalomethanes.

2[The State may require a supplier of water to monitor for MTP at a frequency specified by the State.] A system that is installing granular activated carbon (GAC) or membrane technology to comply with the trihalomethane and haloacetic acid MCLs may apply to the State for an extension of up to 24 months past the compliance dates for those MCLs.  Systems must comply with any interim measures and schedules of compliance set by the State.

Table 3A.  Maximum Residual Disinfectant Level (MRDL) Determination

| Disinfectant | MRDL1 (mg/L) | Type of water system | Determination of MRDL violation |
| --- | --- | --- | --- |
| Chlorine | 4.0 (as Cl2) | Community and NTNC using chlorine or chloramines as disinfectant or oxidant | Compliance is based on a running annual arithmetic average, computed quarterly, of monthly averages of all samples collected by the system. If the running annual average exceeds the MRDL, the system is in violation and must notify the public. |
| Chloramines2 | 4.0 (as Cl2) |  |  |
| Chlorine Dioxide | 0.8 (as ClO2) | Community, NTNC, and Transient Noncommunity using chlorine dioxide as disinfectant or oxidant | Public Health Hazard (Acute Violation) Compliance is based on daily samples collected by the system. If any daily sample taken at the entrance to the distribution system exceeds the MRDL, and on the following day one (or more) of the three samples taken in the distribution system exceeds the MRDL, the system is in violation. |
|  |  |  | Nonacute Violation Compliance is based on daily samples collected by the system. If any two consecutive daily samples taken at the entrance to the distribution system exceed the MRDL, and all distribution system samples taken are below the MRDL, the system is in violation. |

1Systems using surface water or ground water under the direct influence of surface water and serving 10,000 or more people must comply by January 1, 2002.  Systems using surface water or ground water under the direct influence of surface water and serving fewer than 10,000 people, or systems using ground water must comply by January 1, 2004.

2In cases where systems switch between the use of chlorine and chloramines for residual disinfection during the year, compliance must be determined by including together all monitoring results of both chlorine and chloramines.

Table 4A.  Surface Water Turbidity Performance Standards 1

[Maximum Contaminant Level Determination1]

| Contaminant | Filtration type | Performance standard1 | [MCL] | Determination of treatment technique[/MCL] violation |
| --- | --- | --- | --- | --- |
| Filtered water turbidity | Conventional filtration and Direct Filtration | [0.5 NTU2,3] 0.3 NTU2,4,5 | [Not applicable] | A treatment technique violation occurs if more than five percent of the composite filter effluent measurements taken each month exceed the performance standard values. | The turbidity level of representative samples of the filtered water must at no time exceed 1 NTU.4,5 |
|  | Slow sand filtration | 1.0 NTU2[3] |  | A treatment technique violation occurs if more than five percent of the composite filter effluent measurements taken each month exceed the performance standard values. | The turbidity level of representative samples of the filtered water must at no time exceed 5 NTU. |
|  | Diatomaceous earth filtration | 1.0 NTU2[3] |  |  |  |
|  | Alternative filtration | 1.0 NTU2,3 |  |  |  |

1The standards apply to systems with surface water sources or groundwater sources directly influenced by surface water.

[2The performance standard applies to direct filtration and alternative filtration technologies capable of complying with requirement of Subdivision (b) of Section 5-1.30 of this Subpart as demonstrated to the department by pilot studies.]

[3]2NTU = [Nephelomtric] Nephelometric Turbidity Unit

3The performance standard applies to alternative filtration technologies capable of complying with requirement of section 5-1.30(b) of this Subpart as demonstrated to the department by pilot studies, unless the department sets a turbidity performance standard for a specific system.

4Systems serving 10,000 or more people must comply by January 1, 2002. If the combined filter effluent turbidity exceeds 1 NTU, the system must consult with the State in accordance with paragraph 5-1.78(d)(3) of this Subpart.

5Systems serving fewer than 10,000 people must comply by January 14, 2005. If the combined filter effluent turbidity exceeds 1 NTU, the system must consult with the State in accordance with paragraph 5-1.78(d)(3) of this Subpart.  Until January 14, 2005, the performance standard is 0.5 NTU and the turbidity level of representative samples of the filtered water must at no time exceed 5.0 NTU.

Table 8B.  Inorganic Chemicals and Physical Characteristics

# Minimum Monitoring Requirements

| Contaminant | Type of water system | Initial frequency by source type3 | Accelerated sampling7 |
| --- | --- | --- | --- |
|  |  | Groundwater only | Surface only or surface and groundwater |  |
| Antimony Arsenic Barium Beryllium Cadmium Chromium Cyanide Mercury Nickel Selenium Thallium Fluoride | Community and NTNC1,2,6 | One sample per entry point every 3 years by 12/31/958 | One sample per entry point per year9 | If GT MCL, one sample quarterly. 4,5 If LT MCL, maintain initial frequency. |
|  | Transient noncommunity | State discretion10 | State discretion10 | State discretion10 |
| Bromate11 | Community and NTNC using ozone for disinfection or oxidation | One sample per month at each entry point13, 17 | One sample per month at each entry point13, 17 | State discretion10 |
| Chlorite12 | Community and NTNC using chlorine dioxide for disinfection or oxidation | Daily samples at each entry point. Additional three-sample set monthly in the distribution system14, 15, 16, 17 | Daily samples at each entry point. Additional three-sample set monthly in the distribution system14, 15, 16, 17 | State discretion10 |

GT = Greater Than

LT = Less Than

1A waiver from the required initial monitoring frequencies may be granted by the State, based upon the following conditions:

- A minimum of one sample shall be collected while the waiver is effective.

- Surface water systems must have monitored annually for at least three years and groundwater systems must have conducted a minimum of three rounds of monitoring with at least one sample taken since January 1, 1990.

Table 8B.  Inorganic Chemicals and Physical Characteristics

Minimum Monitoring Requirements (continued)

- All results must be less than the MCL.

- New sources are not eligible for a waiver until completion of three rounds of sampling

- Waivers issued by the State shall be made in writing, shall cite the basis for determination and shall not exceed a maximum of nine years.

2To determine the appropriate reduced monitoring frequency, the State shall consider:

- reported concentrations from all previous monitoring

- variations in reported concentrations; and

- other factors which may affect contaminant concentrations such as changes in groundwater pumping rates, changes in the system’s configuration, operating procedures, stream flows or other characteristics

3For all types of water sources the system shall take each sample at the same sampling point unless conditions make another sampling point more representative of each source or

treatment plant.  If a system draws water from more than one source and the sources are combined before distribution, the system must sample at an entry point to the distribution

system during periods of normal operating conditions when water is representative of all sources, or separately at the individual sources.  The State may allow systems to

composite samples in accordance with the conditions in Appendix 5-C.  All samples taken and analyzed in accordance with the monitoring plan must be included in determining compliance, even if the number is greater than the minimum required.

4The State may decrease the quarterly monitoring requirement to the initial sampling requirement provided that it is determined that the system is reliably and consistently below

the MCL on the basis of a minimum of two quarterly groundwater samples and a minimum of four quarterly samples for surface water.

5If concentrations of a listed contaminant exceed the MCL, the Department requires the collection of an additional sample as soon as possible but not to exceed two weeks.

6The State may require or the water system may request more frequent monitoring frequencies than is minimally required.  The State, at its discretion, may require confirmation

samples for positive and negative results.

7The average of the initial and confirmation sample contaminant concentration at each sampling point shall be used to determine compliance with the MCL.

8Systems with fewer than 150 service connections may postpone initial monitoring for antimony, beryllium, cyanide, nickel and thallium until 1998, but no later than three years

after conducting its last result set of analysis for arsenic, barium, cadmium, mercury, selenium and fluoride.

9Systems with fewer than 150 service connections may postpone initial monitoring for antimony, beryllium, cyanide, nickel and thallium until 1996.

10State discretion shall mean requiring monitoring when the State has reason to believe the MCL has been violated, the potential exists for an MCL violation or the contaminant

may present a risk to public health.

Table 8B.  Inorganic Chemicals and Physical Characteristics

Minimum Monitoring Requirements (continued)

11Community and nontransient noncommunity systems using ozone for disinfection or oxidation must comply with the bromate monitoring requirement.  Systems using surface water or ground water under the direct influence of surface water and serving 10,000 or more people must comply by January 1, 2002.  Systems using surface water or ground water under the direct influence of surface water and serving fewer than 10,000 people, or systems using ground water must comply by January 1, 2004.

12Community and nontransient noncommunity systems using chlorine dioxide as a disinfectant or oxidant must comply with the chlorite monitoring requirement.   Systems using surface water or ground water under the direct influence of surface water and serving 10,000 or more people must comply by January 1, 2002.  Systems using surface water or ground water under the direct influence of surface water and serving fewer than 10,000 people, or systems using ground water must comply by January 1, 2004.

13Systems required to analyze for bromate may reduce monitoring from monthly to once per quarter, if the system demonstrates that the average source water bromide concentration is less than 0.05 mg/L based on representative monthly bromide measurements for one year.  A system may remain on reduced bromate monitoring until the running annual average source water bromide concentration, computed quarterly, is equal to or greater than 0.05 mg/L.  If the average bromide concentration is equal to or greater than 0.05 mg/L, the system must resume routine monthly bromate monitoring.

14On each day following a sample result that exceeds the chlorite MCL at the entrance to the distribution system, the system must take three chlorite distribution system samples at the following locations:  as close to the first customer as possible, in a location representative of average residence time, and in a location representative of maximum residence time.  The samples comprising the three-sample set required for routine monitoring must be collected at the same three locations in the distribution system that are used when following up on a daily MCL exceedance at the entry point.  The system may use results of additional monitoring, conducted as the result of an entry point MCL exceedance, to meet the requirement for routine monthly monitoring.

15Daily chlorite monitoring at the entrance to the distribution system may not be reduced.  Monthly chlorite monitoring in the distribution system may be reduced to one three-sample set per quarter after one year of monitoring where no individual chlorite sample taken in the distribution system has exceeded the chlorite MCL.  If the system has had to conduct distribution system monitoring as a result of an MCL exceedance at the entry point, the system cannot reduce monitoring.  The system may remain on a reduced monitoring schedule until either any of the three individual chlorite samples taken quarterly in the distribution system exceeds the chlorite MCL or the system is required to conduct distribution system monitoring because of an entry point chlorite MCL exceedance.

16A system must monitor according to its monitoring plan as described in section 5-1.51(c) of this Subpart.  Failure to monitor in accordance with the monitoring plan is a monitoring violation.

17Failure to monitor will be treated as a monitoring violation for the entire period covered by an annual average where compliance is based on an annual average of monthly or quarterly samples or averages and a system’s failure to monitor makes it impossible to determine MCL compliance.

Table 9A.  Organic Chemicals – [Trihalomethanes] Disinfection Byproducts

# Minimum Monitoring Requirements

| Surface Water Systems, Ground Water Systems Under the Direct Influence of Surface Water, or Combined Surface and Ground Water Systems |
| --- |
| Contaminant | Type of water system | Routine Monitoring Frequency1 | Reduced Monitoring Frequency | Sample Locations in the Distribution System1 |
| Total Trihalomethanes Haloacetic Acids | Community and NTNC serving [10,000 or more] at least 10,000 persons2 | [The supplier of chlorinated water from all source types must collect four samples per quarter per disinfection station.] Four samples per quarter per treatment plant 3,4 | One sample per quarter per treatment plant.3,4,5 | At least 25% of all samples collected each quarter at locations representing maximum residence time. Remaining samples taken at locations representative of at least average residence time in the distribution system and representing the entire distribution system.6 If monitoring has been reduced, sample must be collected at location reflecting maximum residence time. |
|  | Community [serving fewer than 10,000 persons] and NTNC serving 500 to 9,999 persons7 | [State discretion] One sample per quarter per treatment plant 3,4 | One sample per year per treatment plant during month of warmest water temperature.5 | Location representing maximum residence time.6 |
|  | Community and NTNC serving fewer than 500 persons7 | One sample per year per treatment plant collected during the month of warmest water temperature. If the sample (or average of annual samples, if more than one sample is taken) exceeds the MCL, system must increase monitoring to one sample per treatment plant per quarter. | Cannot reduce monitoring. | Location representing maximum residence time.6 |
|  | Transient Noncommunity | State discretion8 | State discretion8 | State discretion8 |

| Table 9A. (continued) Organic Chemicals – Disinfection Byproducts Minimum Monitoring Requirements |
| --- |
| Ground Water Systems Using Chemical Disinfectant |
| Contaminant | Type of water system | Routine Monitoring Frequency1 | Reduced Monitoring | Sample Locations in the Distribution System1 |
| Total Trihalomethanes Haloacetic Acids | Community and NTNC using chemical disinfectant and serving at least 10,000 persons | One sample per quarter per treatment plant.3,4,10 | One sample per year per treatment plant during month of warmest water temperature.9,10 | Locations representing maximum residence time.6 |
|  | Community and NTNC using chemical disinfectant and serving fewer than 10,000 persons7 | One sample per year per treatment plant during month of warmest water temperature.10 If the sample (or average of annual samples, if more than one sample is taken) exceeds the MCL, system must increase monitoring to one sample per treatment plant per quarter, taken at a point reflecting the maximum residence time in the distribution system. | One sample every three years per treatment plant.11 Sample must be collected during month of the year with the warmest water temperature. | Locations representing maximum residence time.6 |
|  | Transient Noncommunity | State discretion8 | State discretion8 | State discretion8 |

1[The state may require a supplier of water to monitor for MTP at a frequency specified by the State.]  A system must monitor according to its monitoring plan as described in section 5-1.51 (c) of this Subpart.  Failure to monitor in accordance with the monitoring plan is a monitoring violation.

2[At least 25% of the quarterly samples must be obtained at distribution points reflecting maximum residence time; the remaining samples must be taken at representative distribution points..  All samples for a quarter must be sampled on the same day.]  Effective January 1, 2002.

3[The State may reduce the TTHM monitoring frequencies at systems which do not exceed the MCL.]  Failure to monitor will be treated as a monitoring violation for the entire period covered by an annual average where compliance is based on an annual average of monthly or quarterly samples or averages and a system’s failure to monitor makes it impossible to determine MCL compliance. If a system fails to complete four consecutive quarters of monitoring, compliance with the MCL will be based on an average of the available data.

4 [State discretion shall mean requiring monitoring when the State has reason to believe the MCL has been violated, the potential exists for an MCL violation or the contaminant may present a risk to public health.]  If, during the first year of monitoring, any individual quarter’s average will cause the annual average of that system to exceed the MCL the system is out of compliance at the end of that quarter.

5System may reduce monitoring if at least one year of samples have been collected and the annual average of total THMs is less than or equal to 0.040 mg/L and the annual average of haloacetic acids is less than or equal to 0.030 mg/L. In order to be eligible for reduced monitoring, the source water annual average total organic carbon (TOC) level, before any treatment, must be less than or equal to 4.0 mg/L.  Systems on a reduced monitoring schedule may remain on that reduced schedule as long as the average of all samples taken in the year is no more than 0.060 mg/L and 0.045 mg/L for total trihalomethanes and haloacetic acids, respectively.  Systems that exceed these levels must  resume monitoring at the routine frequency in the quarter immediately following the exceedance.

6If a system elects to sample more frequently than the minimum required, at least 25% of all samples collected each quarter (including those taken in excess of the required frequency) must be taken at locations that represent the maximum residence time of the water in the distribution system.  The remaining samples must be taken at locations representative of at least average residence time in the distribution system.  A system must sample at locations identified in a monitoring plan approved by the State.

7Effective January 1, 2004.  Until then, monitoring of these systems is at State’s discretion.

8State discretion shall mean requiring monitoring when the State has reason to believe the MCL has been violated, the potential exists for an MCL violation or the contaminant may present a risk to public health.

9System may switch from routine monitoring to reduced monitoring if at least one year of samples have been collected and the annual average of total THMs is less than or equal to 0.040 mg/L and the annual average of haloacetic acids is less than or equal to 0.030 mg/L.  Systems on a reduced monitoring schedule may remain on that reduced schedule as long as the result of the sample for the year is no more than 0.060 mg/L and 0.045 mg/L for total trihalomethanes and haloacetic acids, respectively.  Systems that exceed these levels must resume quarterly monitoring in the quarter immediately following the exceedance.

10The State may allow multiple wells drawing water from a single aquifer to be considered one treatment plant for determining the minimum number of samples required.

11System may reduce monitoring if at least one year of samples have been collected and the annual average of total THMs is less than or equal to 0.040 mg/L and the annual average of haloacetic acids is less than or equal to 0.030 mg/L for two consecutive years, or if the annual average of total THMs is less than or equal to 0.020 mg/L and the annual average of haloacetic acids is less than 0.015 mg/L for one year.  If a system qualifies for reduced monitoring, the three-year cycle will begin on January 1 following the quarter in which the system qualifies.  Systems on a reduced monitoring schedule may remain on that reduced schedule as long as the result of the last sample is no more than 0.060 mg/L and 0.045 mg/L for total trihalomethanes and haloacetic acids, respectively.  Systems that exceed these levels must resume yearly monitoring in the year immediately following the exceedance.

Table 10A.  Turbidity

Minimum Monitoring Requirements

| Contaminant | Type of water system | Source type |
| --- | --- | --- |
|  |  | Groundwater | Surface water1 |
| Filtered water turbidity | Community and Noncommunity | Not applicable | Continuous monitoring for composite filter effluent and individual filters.2,3,4,5 [Every four hours or continuous monitoring for composite filter effluent. Additional monitoring may be required, by the State, for each individual filter to determine compliance with subdivision (b) of section 5-1.30 of this Subpart.2,3,4] |
| Raw water turbidity | Unfiltered surface: Community and Noncommunity | Not applicable | Every four hours or continuous monitoring. [3] 5 |
| Distribution point turbidity | Community Noncommunity | State discretion[5] 7 State discretion[5] 7 | Five distribution samples each week unless otherwise determined by the State. No two samples may be obtained on the same day and no two samples are to be collected from the same distribution point during the same week. State discretion[5] 6 |

1Surface water sources or groundwater sources directly influenced by surface water.

2 Effective January 1, 2002 systems serving 10,000 or more people must record the results of individual filter monitoring every fifteen minutes, and combined filter effluent every four hours. Effective January 14, 2005 systems serving fewer than 10,000 persons must record the results of individual filter monitoring every fifteen minutes, and combined filter effluent every four hours. Until January 14, 2005, systems serving fewer than 10,000 persons must continuously monitor the composite filter effluent turbidity, or record the turbidity every four hours.  The state may allow systems with two filters to monitor the combined filter effluent continuously (recording every 15 minutes) in lieu of monitoring individual filter turbidity. Results of individual filter monitoring must be maintained for at least three years.

3 If there is a failure in the continuous turbidity  monitoring equipment, the system must conduct grab sampling every four hours instead of continuous monitoring, but for no more than five working days following the failure of the equipment.

4 For systems using slow sand filtration or filtration treatment, other than conventional treatment, direct filtration or D.E. filtration, the State may reduce sampling frequency to once  per day if it determines that less frequent monitoring is sufficient to indicate effective filtration performance.

[3] 5If a system uses continuous monitoring, it must use the turbidity values recorded every four hours to determine if a treatment technique violation occurs, unless the State has approved in writing a different time interval.

[5] 6State discretion shall mean requiring monitoring when the State has reason to believe the MCL has been violated, the potential exists for an MCL violation or the contaminant

may present a risk to public health.

Table 13 - REQUIRED NOTIFICATIONS

| Contaminant/Situation (Subpart 5-1 citations) | Single sample exceeds MCL/MRDL | MCL/MRDL/TT1 violation | Failure to meet monitoring requirements and/or failure to use applicable testing procedure |
| --- | --- | --- | --- |
| Public Health Hazard (section 5-1.1(aw)) | Not applicable | State Tier 1 | State Tier 1 |
| Escherichia coli (E. coli) (section 5-1.52 tables 6 and 11) | 2State Not applicable, or 3Tier 1 | State Tier 1 | State 4Tier 3, or Tier 1 |
| Total Coliform (section 5-1.52 tables 6 and 11) | Not applicable | 14State 5Tier 2, or Tier 1 | State Tier 3, or Tier 2 |
| Entry Point Turbidity monthly average (section 5-1.52 tables 4 and 10) | 7State | State Tier 2 | State Tier 3 |
| Entry Point Turbidity two day average (section 5-1.52 tables 4 and 10) | State | State 8Tier 2, or Tier 1 | State Tier 3 |
| Raw Water Turbidity (section 5-1.30(d) and section 5-1.52 table 10A) | State | State 8Tier 2, or Tier 1 | State Tier 3 |
| Filtered Water Turbidity Single exceedance of the maximum allowable Turbidity level (section 5-1.52 tables 4A and 10A) | State | State 8Tier 2, or Tier 1 | State Tier 3 |
| Filtered Water Turbidity Treatment Technique violation (section 5-1.52 tables 4A and 10A) | Not applicable | State Tier 2 | State Tier 3 |
| Distribution Point Turbidity (section 5-1.52 tables 5, 10 and 10A) | Not applicable | State Tier 2 | State Tier 3 |
| 9Treatment Technique violations other than turbidity (section 5-1.30) | Not applicable | State Tier 2 | State Tier 3 |
| 10Free chlorine residual less than 0.2 mg/L at the entry point (section 5-1.30(d)) | Not applicable | 6State | Not applicable |

| Contaminant/Situation (Subpart 5-1 citations) | Single sample exceeds MCL/MRDL | MCL/MRDL/ TT1 violation | Failure to meet monitoring requirements and/or failure to use applicable testing procedure |
| --- | --- | --- | --- |
| Inorganic chemicals and physical characteristics listed in Tables 8A and 8B (section 5-1.52 tables 1, 8A, and 8B) | State | State Tier 2 | State Tier 3 |
| chloride, iron, manganese, silver, sulfate, and zinc (section 5-1.52 tables 1 and 8D) | Not applicable | State Tier 3 | State Tier 3 |
| Sodium (section 5-1.52 tables 1 and 8D) | State if the level exceeds 20 mg/L | Tier 2 if the level exceeds 270 mg/L | Tier 3 |
| Nitrate Nitrite Total Nitrate and Nitrite (section 5-1.52 tables 2 and 8C) | State | State Tier 1 | State 11Tier 1, or Tier 3 |
| Lead and Copper (sections 5-1.40 to 1.49) | Not applicable | State Tier 2 | State Tier 3 |
| Organic Chemicals Group 1 and 2 (section 5-1.52 table 9C) | State | State Tier 2 | State Tier 3 |
| Principal Organic Contaminants Unspecified Organic Contaminants Total POCs and UOCs | State | State Tier 2 | State Tier 3 |
| Radiological Contaminants (section 5-1.52 tables 7 and 12 | State | State Tier 2 | State Tier 3 |
| Monitoring and Control of Disinfection Byproduct Precursors (section 5-1.60 to 5-1.64) | Not applicable | State Tier 2 | State Tier 3 |

| Contaminant/Situation (Subpart 5-1 citations) | Single sample exceeds MCL/MRDL | MCL/MRDL/ TT1 violation | Failure to meet monitoring requirements and/or failure to use applicable testing procedure |
| --- | --- | --- | --- |
| Disinfectant residuals Chlorine and Chloramine (section 5-1.52 tables 3A and 15) | State | State Tier 2 | State Tier 3 |
| Disinfectant residual Chlorine dioxide At entry point (section 5-1.52 tables 3A and 15) | State | State Tier 2 | State 12Tier 3, or Tier 2 |
| Disinfectant residual Chlorine dioxide In distribution system (section 5-1.52 tables 3A and 15) | State | State 13Tier 1 | State 13Tier 1 |
| Disinfection byproducts Trihalomethanes Haloacetic acids (Tables 3 and 9A) and Bromate and Chlorite (section 5-1.52 tables 1 and 8B) | Not applicable | State Tier 2 | State Tier 3 |
| Acrylamide and Epichlorohydrin (section 5-1.51(j)) | Not applicable | State Tier 2 | Not applicable |
| Operation under a variance or exemption | Not applicable | Tier 3 | Not applicable |
| Violation of conditions of a variance or exemption | Not applicable | State Tier 2 | Not applicable |
| Disruption of water service of four hours or more (section 5-1.23(b)) | Not applicable | 6State | Not applicable |

1MCL-maximum contaminant level, MRDL-maximum residual disinfectant level, TT-treatment technique

2State notification must be made by the supplier of water within 24 hours of learning of an E. coli positive sample.

3Public notification normally does not have to be issued for an E. coli positive sample prior to the results of the repeat samples.  However, there may be situations where the State determines that a Tier 1 notification is necessary to protect the public health.  The supplier of water must provide the Tier 1 notification no later than 24 hours after learning of the State’s determination.

4Failure to test for E. coli requires a Tier 1 notification if testing is not done after any repeat sample tests positive for coliform.  All other E. coli monitoring and testing procedure violations require Tier 3 notification.

5Tier 2 notification is normally required, however, there may be situations where the State determines that a Tier 1 notification is necessary to protect the public health.  The supplier of water must provide the Tier 1 notification no later than 24 hours after learning of the State’s determination.

6Tier 1 notification is required if the situation meets the definition of a public health hazard.

7If the daily entry point analysis exceeds one NTU, a repeat sample must be taken as soon as practicable and preferably within one hour.  If the repeat sample exceeds one NTU, the supplier of water must make state notification.

8Systems must consult with the State within 24 hours after learning of the violation.  Based on this consultation, the State may subsequently decide to elevate the violation from a Tier 2 to a Tier 1 notification.  If consultation does not take place within the 24 hour period, the water system must distribute a Tier 1 notification no later than 48 hours after the system learns of the violation.

9These violations include the following: failure to comply with the treatment technique or monitoring requirements in section 5-1.30(b), (c), and (g) of this Subpart; failure to comply with the avoidance criteria in section 5-1.30(c) of this Subpart; and failure to install filtration or disinfection treatment facilities required by section 5-1.30 of this Subpart; failure to report to the state information required in paragraph (3) of section 5-1.72(c) of this Subpart; and failure to maintain records required in paragraph (7) of section 5-1.72(c) of this Subpart.

10Applies to systems that have surface water or groundwater directly influenced by surface water as a source and use chlorine.  The system must make State notification whether the residual was restored to at least 0.2 mg/L within four hours.

11Failure to take a confirmation sample within 24 hours for nitrate or  nitrite after an initial sample exceeds the MCL requires a Tier 1 notification.  Other monitoring violations for nitrate or nitrite require a Tier 3 notification.

12Failure to monitor for chlorine dioxide at the entrance to the distribution system the day after exceeding the MRDL at the entrance to the distribution system requires a Tier 2 notification.  Other monitoring violations for chlorine dioxide at the entrance to the distribution system require a Tier 3 notification.

13If any daily sample taken at the entrance to the distribution system exceeds the MRDL for chlorine dioxide and one or more samples taken in the distribution system the next day exceed the MRDL, Tier 1 notification is required.  Failure to take the required samples in the distribution system the day after the MRDL is exceeded at the entry point also triggers Tier 1 notification.

14State notification must be made by the supplier of water within 24 hours of learning of the violation.

Table 15.  Disinfection Monitoring for Systems Using Chlorine or Chloramines

Grab Sample Frequency Instead of Continuous Monitoring

Entry Point Filtered and Unfiltered Surface Sources1

| Population served | Samples per day2 |
| --- | --- |
| Up to 500 | 1 |
| 501 – 1,000 | 2 |
| 1,001 - 2,500 | 3 |
| 2,501 – 3,300 | 4 |
| More than 3,300 | Routine grab samples not allowed3 |

1If at any time the [disinfection] chlorine residual concentration falls below 0.2 mg/L the system must collect and analyze a grab sample every four hours until the [disinfection] chlorine residual concentration is again equal to or greater than 0.2 mg/L.

2The day’s grab samples may not be conducted at the same time.

3If there is a failure in the continuous monitoring equipment, grab samples, every four

hours, may be conducted in lieu of continuous monitoring, but for no more than five

working days following the failure of the equipment.

Table 15A.  Disinfectant Residual

Minimum Monitoring Requirements

| Disinfectant | Type of Water System | Routine Monitoring |
| --- | --- | --- |
| Chlorine Chloramines | Community and Nontransient Noncommunity | Sample at the same time and same points in the distribution system as total coliform sampling1 |
| Chlorine Dioxide2 | Community, Nontransient Noncommunity and Transient Noncommunity | Daily sample at the entrance to the distribution system3 |

1CWS using surface water or ground water under the direct influence of surface water may use heterotrophic plate count results of equal to or less than 500 colonies per milliliter as equivalent to a free chlorine residual as outlined in table 11, footnote 6 in lieu of taking separate samples for disinfection residuals.

2Monitoring is required if chlorine dioxide is used for either oxidation or disinfection.

3If the MRDL of 0.8 mg/L is exceeded, the system must take three samples in the distribution system on the following day.  If chlorine dioxide or chloramines are used to maintain a disinfectant residual in the distribution system, or if chlorine is used and there are no rechlorination stations, the system must take 3 samples as close to the first customer as possible, at intervals of at least 6 hours.  If chlorine is used and there is a rechlorination station, the system must take one sample as close to the first customer as possible, one sample representing average residence time, and one sample representing maximum residence time.

New Sections 5-1.60, 5-1.61, 5-1.62 and 5-1.63 are added as follows:

### MONITORING AND CONTROL OF DISINFECTION BYPRODUCT PRECURSORS

### 5-1.60 Applicability.  Surface water systems or systems using ground water under the direct influence of surface water that are community or nontransient noncommunity systems and use conventional filtration treatment must operate with enhanced coagulation to achieve the total organic carbon (TOC) percent removal levels specified in section 5-1.63 of this Subpart, unless the system meets the alternative compliance criteria described in section 5-1.62 of this Subpart.  Systems serving 10,000 or more people must comply with this requirement beginning January 1, 2002.  Systems serving fewer than 10,000 people must comply with this requirement beginning January 1, 2004.

5-1.61 Monitoring requirements for disinfection byproduct precursors.  Surface water systems and systems using ground water under the direct influence of surface water that are community or nontransient noncommunity systems and use conventional filtration treatment must monitor each treatment plant for TOC.  Samples to be analyzed for TOC must be collected no further downstream than the point of combined filter effluent turbidity monitoring and representative of the treated water.  TOC monitoring shall be conducted in accordance with the system’s monitoring plan described in subdivision 5-1.51 (c) of this Subpart.  These same systems must also monitor for TOC in the source water prior to any treatment at the same time as they are monitoring for TOC in the treated water.  These samples (source water and treated water) are referred to as paired samples.  At the same time as the source water sample is taken, all systems must monitor for alkalinity in the source water prior to any treatment.  Systems must take one paired TOC sample and one source water alkalinity sample per month per plant at a time representative of normal operating conditions and influent water quality.  Systems monitoring for TOC with an average treated water TOC of less than 2.0 mg/L for two consecutive years, or less than 1.0 mg/L for one year, may reduce monitoring for both TOC and alkalinity to one paired TOC sample and one source water alkalinity sample per plant per quarter.  The system must revert to routine monitoring in the month following the quarter when the annual average treated water TOC is greater than or equal to 2.0 mg/L.

5-1.62 Alternative compliance criteria for enhanced coagulation.  Systems may use one of the following alternative compliance criteria instead of enhanced coagulation:

(a)	The system’s source water TOC level is less than or equal to 2.0 mg/L, calculated quarterly as a running annual average.

(b)	The system’s treated water TOC level is less than or equal to 2.0 mg/L, calculated quarterly as a running annual average.

(c)	The system’s source water SUVA, prior to any treatment and measured monthly, is less than or equal to 2.0 L/mg-m, calculated quarterly as a running annual average.

(d)  	The system’s treated water SUVA, measured monthly, is less than or equal to 2.0 L/mg-m, calculated quarterly as a running annual average.

(e)	The system’s source water TOC level is less than 4.0 mg/L, calculated quarterly as a running annual average; the source water alkalinity is greater than 60 mg/L (as CaCO3), calculated quarterly as a running annual average; and the TTHM and HAA5 running annual averages are no greater than 0.040 mg/L and 0.030 mg/L, respectively.  Alternatively, the system's source water TOC level is less than 4.0 mg/l, calculated quarterly as a running annual average; the source water alkalinity is greater than 60 mg/L (as CaCO3), calculated quarterly as a running annual average; and prior to the effective date for compliance, the system has made a clear and irrevocable financial commitment to use technologies that will limit the levels of TTHMs and HAA5 to no more than 0.040 mg/L and 0.030 mg/L, respectively.  Systems must submit evidence of a clear and irrevocable financial commitment, in addition to a schedule containing milestones and periodic progress reports for installation and operation of appropriate technologies, to the State for approval not later than the effective date for compliance in section 5-1.60 of this Subpart.  These technologies must be installed and operating not later than June 16, 2005.  Failure to install and operate these technologies by the date in the approved schedule will constitute a violation.

(f)	The TTHM and HAA5 running annual averages are no greater than 0.040 mg/L and 0.030  mg/L, respectively, and the system uses only chlorine for primary disinfection and maintenance of a residual in the distribution system.

Systems using the alternative compliance criteria stated in this section must still comply with the monitoring requirements stated in section 5-1.61 of this Subpart.

5-1.63 Enhanced coagulation performance requirements.  Systems must achieve the percent reduction of TOC specified in subdivision (a) of this section (Step 1) between the source water and the combined filter effluent, unless the State approves a system’s request for alternate minimum TOC removal (Step 2) requirements, which are provided in subdivision (d) of this section.

(a)	Required (Step 1) TOC reductions, which are provided in the following table, are based upon specified source water TOC and alkalinity levels:

| (Step 1) Required Removal of TOC by Enhanced Coagulation for Surface Water Systems or Systems Using Ground Water Under the Direct Influence of Surface Water that Use Conventional Filtration Treatment |
| --- |
| Source Water TOC (mg/L) | Source Water Alkalinity |
|  | 0–60 mg/L as CaCO3 (percent removal required) | >60–120 mg/L as CaCO3 (percent removal required) | >120 mg/L as CaCO3 (percent removal required) |
| >2.0 – 4.0 | 35.0 | 25.0 | 15.0 |
| >4.0 – 8.0 | 45.0 | 35.0 | 25.0 |
| >8.0 | 50.0 | 40.0 | 30.0 |

(b)	Systems that must comply with the requirements contained in subdivision (a) of this section must calculate compliance using the method provided in either paragraph (1) of this subdivision or the applicable provisions of paragraph (2) of this subdivision.

(1)	Systems must calculate compliance quarterly, beginning after the system has collected 12 months of data, by determining an annual average using the following method:

(i)	Determine actual monthly TOC percent removal, equal to:  (1 – (treated water TOC/source water TOC)) X 100.

(ii)	Determine the required monthly TOC percent removal from either subdivision (a) or (d) of this section.

(iii)	Divide the value in subparagraph (i) of this paragraph by the value in subparagraph (ii) of this paragraph.

(iv)	Add together the results of subparagraph (iii) of this paragraph for the last 12 months and divide by 12.

(v)	If the value calculated in subparagraph (iv) of this paragraph is less than 1.00, the system is not in compliance with the TOC percent removal requirements.

(2)	Systems may use the provisions in subparagraphs (i) through (iii) of this paragraph instead of the calculations in paragraph (1) of this subdivision to determine compliance with TOC percent removal requirements.

(i)	In any month that the system’s treated or source water TOC level is less than or equal to 2.0 mg/L, the system may assign a monthly value of 1.00 (instead of the value calculated in paragraph (1) of this subdivision) when calculating compliance under the provisions of subdivision (a) of this section.

(ii)	In any month that the system’s source water SUVA, prior to any treatment, is less than or equal to 2.0 L/mg-m, the system may assign a monthly value of 1.00 (instead of the value calculated in paragraph (1) of this subdivision) when calculating compliance under the provisions of subdivision (a) of this section.

(iii)	In any month that the system’s finished water SUVA is less than or equal to 2.0 L/mg-m, the system may assign a monthly value of  1.00 (instead of the value calculated in paragraph (1) of this subdivision) when calculating compliance under the provisions of subdivision (a) of this section.

(c)	Systems that cannot achieve the (Step 1) TOC removals required by subdivision (a) of this section due to water quality parameters or operational constraints must apply to the State, within three months of failure to achieve the TOC removals required by (Step 1), for approval of alternate minimum TOC removal (Step 2) requirements, described in subdivision (d) of this section.  Until the State approves the alternate minimum TOC removal (Step 2) requirements, the system must meet the (Step 1) TOC removals contained in subdivision (a) of this section.

(d)	Alternate minimum TOC removal (Step 2) requirements.  Applications made to the State by enhanced coagulation systems for approval of alternate minimum TOC removal (Step 2) requirements must include, as a minimum, results of bench- or pilot-scale testing conducted using the methodology prescribed in paragraph (1) of this subdivision to determine the alternate enhanced coagulation level.  Applications for alternate minimum TOC (Step 2) requirements must be approved by the State before they can replace the previous (Step 1) TOC removal requirements. The alternate TOC removal is determined by the method described in paragraphs (1) through (5) of this subdivision.

(1)	The alternate minimum TOC removal is the percentage of TOC removed at the point where an incremental addition of 10 mg/L  of alum, or equivalent amount of iron coagulant (ferric salt), results in a TOC removal of (0.3 mg/L.  This TOC removal percentage is then defined as the minimum TOC removal required for the system.  Once approved by the State, this minimum TOC removal requirement supersedes the minimum TOC (Step 1) removal required by the table in subdivision (a) of this section.  This requirement will be effective until such time as the State approves a new value based on the results of a new bench- and pilot-scale test.  Failure to achieve State-set alternative minimum TOC removal levels is a violation.

(2)	Bench- or pilot-scale testing of enhanced coagulation must be conducted by using representative water samples and adding 10 mg/L increments of alum, or equivalent amounts of iron coagulant, until the pH is reduced to a level less than or equal to the enhanced coagulation (Step 2) target pH shown in the following table:

| Enhanced Coagulation Step 2 Target pH |
| --- |
| Alkalinity (mg/L as CaCO3) | Target pH |
| 0 – 60 | 5.5 |
| >60 – 120 | 6.3 |
| >120 – 240 | 7.0 |
| >240 | 7.5 |

(3)	For waters with alkalinities of less than 60 mg/L for which addition of small amounts of alum or equivalent addition of iron coagulant drives the pH below 5.5 before significant TOC removal occurs, the system must add necessary chemicals to maintain the pH between 5.3 and 5.7 in samples until the TOC removal of 0.3 mg/L per 10 mg/L alum added, or equivalent addition of iron coagulant, is reached.

(4)	The system may operate at any coagulant dose or pH necessary (consistent with the State Sanitary Code) to achieve the minimum TOC percent removal approved under paragraph (1) of this section.

(5)	If the TOC removal is consistently less than 0.3 mg/L of TOC per 10 mg/L of incremental alum dose at all dosages of alum (or equivalent addition of iron coagulant), the water is deemed to contain TOC not amenable to enhanced coagulation.  The system may then apply for a waiver of enhanced coagulation requirements.

Subdivision (c) of Section 5-1.72 is amended to read as follows:

(c)	Complete daily records shall be kept of the operation of a public water system on forms provided or approved by the department.

(1) 	A copy of such records shall be sent to the State by the 10th calendar day of the next reporting period. These records shall include the results of all tests, measurements or analysis required to be made by this Subpart or as requested by the State. Other operational records shall be available for inspection by the State.

(2)	Systems using conventional filtration treatment or direct filtration must conduct continuous turbidity monitoring for each individual filter, as described in section 5-1.52 table 10A.  Systems must record the results of individual filter monitoring every 15 minutes.  Systems must maintain individual filter monitoring results for at least three years.  Systems must report to the State that they have conducted individual filter turbidity monitoring within 10 days after the end of each month the system serves water to the public.  Systems must report to the State individual filter turbidity measurement results within 10 days after the end of each month the system serves water to the public only if measurements demonstrate one or more of the following conditions, except that systems serving fewer than 10,000 persons are not required to comply with subparagraph (ii) of this paragraph:

(i)	For any individual filter that has a measured turbidity level of greater than 1.0 Nephelometric Turbidity Units (NTU) in two consecutive measurements taken 15 minutes apart, the system must report the filter identification number, the turbidity measurement, and the date(s) on which the exceedance occurred.  In addition, the system must either produce a filter profile for the filter within seven days of the exceedance (if the system is not able to identify an obvious reason for the abnormal filter performance) and submit the profile to the State, or report the obvious reason for the exceedance.

(ii)	For any individual filter that has a measured turbidity level of greater than 0.5 NTU in two consecutive measurements taken 15 minutes apart at the end of the first four hours of continuous filter operation after the filter has been backwashed or otherwise taken offline, the system must report the filter number, the turbidity, and the date(s) on which the exceedance occurred.  In addition, the system must either produce a filter profile for the filter within seven days of the exceedance (if the system is not able to identify an obvious reason for the abnormal filter performance) and submit the profile to the State, or report the obvious reason for the exceedance.

(iii)	For any individual filter that has a measured turbidity level of greater than 1.0 NTU in two consecutive measurements taken 15 minutes apart at any time in each of three consecutive months, the system must report to the State the filter number, the turbidity measurement, and the dates on which the exceedance occurred.  In addition, the system must conduct a self-assessment of the filter within 14 days of the exceedance and submit the self-assessment to the State.  The self-assessment must consist of at least the following components: assessment of filter performance; development of a filter profile; identification and prioritization of factors limiting filter performance; assessment of the applicability of corrections; and preparation of a filter self-assessment report.

(iv)	For any individual filter that has a measured turbidity level of greater than 2.0 NTU in two consecutive measurements taken 15 minutes apart at any time in each of two consecutive months, the system must report to the State the filter number, the turbidity measurement, and the dates on which the exceedance occurred.  In addition, the system must arrange for the conduct of a comprehensive performance evaluation (CPE) by the State or a third party approved by the State no later than 30 days following the exceedance, and have the evaluation completed and submitted to the State no later than 90 days following the exceedance.

(3)	Systems using conventional filtration treatment or direct filtration treatment must notify the State in writing by December 8, 2003, if the system recycles spent filter backwash water, thickener supernatant, or liquids from dewatering processes.  This notification must include, at a minimum, the following information:

(i)	A plant schematic showing the origin of all flows which are recycled (including, but not limited to, spent filter backwash water, thickener supernatant, and liquids from dewatering processes), the hydraulic conveyance used to transport them, and the location where they are reintroduced back into the treatment plant; and

(ii)	Typical recycle flow in gallons per minute (gpm), the highest observed plant flow experienced in the previous year (gpm), design flow for the treatment plant (gpm), and the State-approved operating capacity for the plant where the State has made such determinations.

Subdivision (d) of Section 5-1.72 is amended to include a new paragraph (7) to read as follows:

(7)	Beginning June 8, 2004, systems using conventional filtration treatment or direct filtration that recycle spent backwash water, thickener supernatant or liquids from the dewatering processes must collect the following recycle flow information:

(i)	Copy of the recycle notification and information submitted to the State in accordance with paragraph (3) of subdivision (c) of this section.

(ii)	List of all recycle flows and the frequency with which they are returned.

(iii)	Average and maximum backwash flow rate through the filters and the average and maximum duration of the filter backwash process in minutes.

(iv)	Typical filter run length and a written summary of how filter run length is determined.

(v)	The type of treatment provided for the recycle flow.

(vi) 	Data on the physical dimensions of the equalization and/or treatment units, typical and maximum hydraulic loading rates, type of treatment chemicals used and average dose and frequency of use, and frequency at which solids are removed, if applicable.

Paragraph (2) of Subdivision 5-1.72(f) is amended to read as follows:

(2)	Definitions for Maximum Contaminant Level,  [and] Maximum Contaminant Level Goal, Maximum Residual Disinfectant Level, and Maximum Residual Disinfectant Level Goal.  Each report must include the definitions [included in this paragraph, for Maximum Contaminant Level (MCL), and Maximum Contaminant Level Goal (MCLG),] set forth using the following language:

(i)	Maximum Contaminant Level Goal (MCLG):  The level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs allow for a margin of safety.

(ii)	Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water.  MCLs are set as close to the MCLGs as feasible.

(iii)	Maximum Residual Disinfectant Level (MRDL): The highest level of a disinfectant that is allowed in drinking water.

(iv)	Maximum Residual Disinfectant Level Goal (MRDLG):  The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

Paragraph (12) of Subdivision 5-1.72(f) is amended to read as follows:

(12)	Additional health effects statements for arsenic, nitrate, lead, [and] total trihalomethanes[:], and fluoride.

(i)	a system which detects arsenic at levels above [25] 5 ug/l, but below the MCL must include in its report a short informational statement about arsenic, using language prescribed by the State.

(ii)	a system which detects nitrate at levels above 5 mg/l, but below the MCL must include a short informational statement about the impacts of nitrate on children using language prescribed by the State.

(iii)	a system which detects lead above the action level in more than 5%, and up to and including 10% of the sites sampled (or for systems sampling less than 20 sites and even one sample is above the action level) must include a short informational statement about the special impact of lead on children using language prescribed by the State.

(iv)	a system using only ground water or using surface water as its source and serving less than 10,000 persons, which detects TTHMs above 80 ug/l, but below 100 ug/l, as an annual average, monitored and calculated as described in Section 5-1.52 Table 3, must until January 1, 2004, include health effects language prescribed by the State.

(v)	a system which detects fluoride at levels above 2 mg/l, but below the MCL must include in its report an informational statement about fluoride, using language prescribed by the State.

A new paragraph (15) is added to subdivision 5-1.72(f) as follows:

(15)	Information on unregulated contaminants.  If the system was required to monitor for contaminants listed in section 5-1.52 Table 16, the report must identify a person and provide the telephone number to contact for information on the monitoring results.

Paragraph (3) of subdivision 5-1.72 (g) is amended to read as follows:

(3)       Recordkeeping requirements.   Any system subject to this Subpart must retain copies of the report for no less than [five] three years.

Subdivision 5-1.74 (a) is amended to read as follows:

(a)	For determining compliance with the Subpart, results of analyses may be considered only if they have been performed by an environmental laboratory approved in accordance with Subpart 55-2 of Part 55 of the administrative rules and regulations of the State (10 NYCRR Part 55, Subpart 55-2).  However, measurements for pH, temperature, turbidity, disinfectant residual, alkalinity, calcium, orthophosphate, bromide, chlorite, total organic carbon (TOC) concentration, dissolved organic carbon concentration, ultraviolet (UV) absorption at 254 nanometers, and silica may be performed by any person with a demonstrated ability to perform these analyses.

Section 5-1.77 is amended to read as follows:

5-1.77 [Public health hazard] State notification.

- [Notwithstanding anything to the contrary contained in sections 5-1.12, 5-1.23, 5-1.30, 5-1.51 and 5-1.52 table 13 of this Subpart, the] The supplier of water shall make State notification within 24 hours of learning of the existence or potential existence of  [when a condition exists that may constitute] a public health hazard[.], or within 48 hours for any other violation or situation that may pose a risk to public health.  Section 5-1.52 table 13 of this Subpart lists violations and situations that require State notification.

(b)	The information provided in a State notification shall include, but not be limited to, the following:

(1)	a description of the violation or situation, including the contaminant of concern, and (as applicable) the contaminant level;

(2)	when the violation or situation occurred;

(3)	what the system is doing to correct the violation or situation; and

(4)	when the water system expects to return to compliance.

[(b)	Notwithstanding anything to the contrary contained in sections 5-1.12, 5-1.23,

5-1.51 and 5-1.52, table 13 of this Subpart, the supplier of water shall make public notification when, on the determination and at the direction of the commissioner, a condition exists which constitutes a public health hazard.  The supplier of water must also notify the chief administrative and/or elected official of the city, village or town, wherein the public water system is located, and the local law enforcement department having jurisdiction in the area served by the public water system, by telephone, that a public health hazard exists.  If there is a potential for the public health hazard to cross political boundaries, all potentially impacted chief administrative and/or elected officials and local law enforcement departments in the political subdivisions, served by the public water system, must also be notified.]

Section 5-1.78 is REPEALED and a new Section 5-1.78 is added to read as follows:

5-1.78 Public Notification

(a)	General public notification requirements. Each owner or operator of a public water system must provide public notification for public health hazards, and for all MCL, MRDL, treatment technique, monitoring and testing procedure violations, and for other situations posing a risk to public health.  Public notification requirements are divided into three tiers to take into account the seriousness of the violation or situation and any potential adverse health effects that may be involved.  The form, manner, frequency, and other requirements for each tier are described in subdivisions (c)-(e) of this section.  Section 5-1.52 table 13 of this Subpart lists the required public notification (Tier 1, Tier 2, or Tier 3) for specific violations and other situations posing a risk to public health.

(1)	Public water systems that sell or otherwise provide drinking water to other public systems (i.e. to consecutive systems) are required to give public notice to the owner or operator of the consecutive system; the consecutive system is responsible for providing public notification to the persons it serves.

(2) 	If a public water system can show that a violation in a portion of the distribution system is physically or hydraulically isolated from other parts of the distribution system, then with written permission from the State the system may limit the notice to only persons served by that portion of the system that is out of compliance.

(3)	The public water system, within 10 days of completing the public notification requirements under this Subpart for the initial public notification and any repeat notices, must submit to the State a certification that it has fully complied with the public notification regulations.  The public water system must include with this certification a representative copy of each type of notice distributed, published, posted, and made available to the persons served by the system and to the media.  Copies of public notices and certificates issued pursuant to this paragraph must be kept by the supplier of water for three years after issuance.

(b)	Content, presentation, and standard language requirements for all public notifications.

(1)	When a public water system has a violation or a situation posing a risk to public health, other than operating under a variance or exemption, the public notification must include the following elements:

(i)	a description of the violation or situation, including the contaminant of concern, and (as applicable) the contaminant level;

(ii)	when the violation or situation occurred;

(iii)	any potential adverse health effects from the violation or situation, including the standard language under subparagraph (b)(4)(i) or (b)(4)(ii) of this section, whichever is applicable;

(iv)	the population at risk, including subpopulations particularly vulnerable if exposed to the contaminant in their drinking water;

(v)	whether alternative water supplies should be used;

(vi)	what actions consumers should take, including when they should seek medical help, if known;

(vii)	what the system is doing to correct the violation or situation;

(viii)	when the water system expects to return to compliance;

(ix)	the phone number of the water system owner, operator, or designee of the public water system as a source of additional information concerning the notice;

(x)	the phone number of the county or district health department which has jurisdiction over the water system; and

(xi)	a statement included in notices distributed by mail or direct delivery to encourage the notice recipient to distribute the public notice to other persons served, using the standard language under subparagraph (b)(4)(iii) of this section.

(2)	When a public water system operates under a variance or exemption, each public notice must include the following elements:

(i)	an explanation of the reasons for the variance or exemption;

(ii)	the date on which the variance or exemption was issued;

(iii)	a brief status report on the steps the system is taking to install treatment, find alternative sources of water, or otherwise comply with the terms and schedules of the variance or exemption; and

(iv)	a notice of any opportunity for public input in the review of the variance or exemption.

(3)	Notice presentation.  Each public notice required by this section:

(i)	must be displayed in a conspicuous way (where applicable);

(ii)	must not contain overly technical language or very small print;

(iii)	must not be formatted in a way that defeats the purpose of the notice;

(iv)	must not contain language which nullifies the purpose of the notice; and

(v)	must contain information for non-English speaking consumers, where appropriate.  For systems serving a large proportion of non-English speaking consumers, as determined by the State, the notice must contain information prescribed by the State in the appropriate language(s) expressing the importance of the notice.

(4)	Standard Language.

(i)	Mandatory health effects language must be included in the notification for MCL and MRDL violations, treatment technique violations, and violations of the condition of a variance or exemption. The mandatory health effects language will be developed by the Department and provided to the supplier of water by the State.

(ii)	Standard language for monitoring and testing procedure violations.  Public water systems must include the following language in their notice, including the language necessary to fill in the blanks, for all monitoring and testing procedure violations listed in section 5-1.52 table 13: We are required to monitor your drinking water for specific contaminants on a regular basis.  Results of regular monitoring are an indicator of whether or not your drinking water meets health standards.  During (compliance period), we “did not monitor or test” or “did not complete all monitoring or testing” for (contaminant(s)), and therefore cannot be sure of the quality of your drinking water during that time.

(iii)	Standard language to encourage distribution of the public notice to all persons served, when the notice is distributed by mail or direct delivery:  Please share this information with all the other people who drink this water, especially those who may not have received this notice directly (for example, people in apartments, nursing homes, schools, and businesses).  You can do this by posting this notice in a public place or distributing copies by hand or mail.

(c)	Tier 1 notification requirements (public health hazards, as defined in subdivision 5-1.1(aw) of this Subpart, require Tier 1 notification).  The supplier of water must:

(1)	provide public notification no later than 24 hours after the system learns of a public health hazard;

(2)	initiate consultation with the State no later than 24 hours after the public water system learns of the public health hazard, and comply with any additional notification requirements established as a result of the consultation (including using additional forms of delivery for the initial notification, the duration of the posted notices, or any repeat notices);

(3)	notify by telephone the chief administrative or elected official of the city, village or town, wherein the public water system is located, and the local law enforcement department having jurisdiction in the area served by the public water system, that a public health hazard exists.  If there is a potential for the public health hazard to cross political boundaries, all potentially impacted chief administrative or elected officials and local law enforcement departments in the political subdivisions, served by the public water system, must also be notified; and

(4)	provide the notice in a form and manner reasonably calculated to reach all persons served (including residential, transient, and non-transient users) in the required time period.  Water systems are to use one or more of the following forms of delivery:

(i)	appropriate broadcast media (such as radio and television);

(ii)	posting of the notice in conspicuous locations throughout the area served by the water system;

(iii)	hand delivery of the notice to persons served by the water system; or

(iv)	another delivery method approved in writing by the State.

(d)	Tier 2 notification requirements (section 5-1.52 table 13 of this Subpart lists violations and situations that require Tier 2 notification).

(1)	The supplier of water must provide public notification no later than 30 days after the system learns of  a violation or situation that requires Tier 2 notification.  If the public water system corrects the violation within 30 days, the State may allow additional time for the initial notice of up to three months from the date the system learns of the violation.

(2)	The supplier of water must repeat the notice every three months as long as the violation or situation persists.  If the public notice is posted, the notice must remain in place as long as the violation or situation persists, but in no case less than seven days.

(3)	For the turbidity violations or exceedances specified in subparagraphs (i)-(iii) of this paragraph, the supplier of water must consult with the State no later than 24 hours after the public water system learns of the violation or exceedance to determine whether a Tier 1 notification is required to protect public health.  When consultation does not take place within the 24 hour period, the water system must distribute a Tier 1 notification no later than 48 hours after the system learns of the violation or exceedance.  Consultation with the State is required for:

(i)	a violation of the two day average maximum allowable turbidity at the entry point pursuant to section 5-1.52 table 4 of this Subpart;

(ii)	a violation resulting from a single exceedance of the maximum allowable turbidity for filter effluent pursuant to section 5-1.52 table 4A of this Subpart; and

(iii)	a single raw water turbidity exceedance of 5 NTU for systems operating under the avoidance criteria in subdivision 5-1.30(c) of this Subpart.

(4)	The supplier of water must provide the notice in a form and manner reasonably calculated to reach all persons served in the required time period.

(i)	Unless directed otherwise by the State in writing, community water systems must provide notice by: mail or other direct delivery to each customer receiving a bill, and to other service connections to which water is delivered by the public water system; and by any other method reasonably calculated to reach other persons regularly served by the system if they would not normally be reached by mail or direct delivery.

(ii)	Unless directed otherwise by the State in writing, non-community water systems must provide notice by posting the notice in conspicuous locations, and by any other method(s) reasonably calculated to reach other persons served by the system if they would not normally be reached by posting.

(e)	Tier 3 notification requirements (section 5-1.52 table 13 of this Subpart lists violations and situations that require Tier 3 notification).

(1)	The supplier of water for community and non-transient noncommunity water systems must provide public notification no later than one year after the system learns of a violation or situation that requires Tier 3 notification.  The supplier of water for transient noncommunity water systems must provide public notification no later than 30 days after the system learns of a violation or situation that requires Tier 3 notification.  If the public water system operates seasonally, the public notification must also be provided before the system closes for the season.

(2)	The supplier of water must repeat the notice annually for as long as the violation or situation persists.  If the public notice is posted, the notice must remain in place as long as the violation or situation persists, but in no case less than seven days.

(3)	The supplier of water may use a single public notice for multiple violations or situations that require Tier 3 notification, as long as the timing requirements of paragraph (1) of this subdivision are met.  Community water systems may use the annual water supply statement (report) (see subdivisions 5-1.72(e) – (h) of this Subpart) to provide Tier 3 notification.

(4)	The supplier of water must provide the initial notice and any repeat notices in a form and manner reasonably calculated to reach all persons served in the required time period.

(i)	Unless directed otherwise by the State in writing, community water systems must provide notice by: mail or other direct delivery to each customer receiving a bill, and to other service connections to which water is delivered by the public water system; and by any other method reasonably calculated to reach other persons served by the system if they would not normally be reached by mail or direct delivery.

(ii)	Unless directed otherwise by the State in writing, non-community water systems must provide notice by posting the notice in conspicuous locations, and by any other method(s) reasonably calculated to reach other persons served by the system if they would not normally be reached by posting.

(f)	Notice to new billing units or new customers.  Community water systems must give a copy of the most recent public notice for any continuing violation, the existence of a variance or exemption, or other ongoing situations requiring a public notice to all new billing units or new customers prior to or at the time service begins.

(g) 	Information on unregulated contaminants.  Nontransient noncommunity water systems that are required to monitor for contaminants listed in section 5-1.52 table 16, must post a notice that identifies a person and telephone number to contact for information on the monitoring results.  The notice must be posted in conspicuous locations and no later than 12 months after the results are known.

(h)	Notice by the State on behalf of the public water system.  The State may make public notification if the State determines that the public's interest will be best served, or if the State determines that the supplier of water is not acting or cannot act in a timely manner.  The State may charge and collect from the supplier of water the cost of making such notification.  However, the supplier of water remains legally responsible for ensuring that the requirements of this section are met.

Subdivision (d) of Section 5-1.91 is amended to read as follows:

(d)	The technologies listed in this section are the best technology, treatment techniques, or other means available for achieving compliance with the maximum contaminant levels for organic chemicals listed in section 5-1.52 table 3 of  this Subpart:

BEST AVAILABLE TECHNOLOGIES (BATs)

| Contaminant | Best Available Technologies |
| --- | --- |
|  | PTA1 | GAC2 | OX3 |
| Benzene | x | x |  |
| Carbon tetrachloride | x | x |  |
| 1,2-Dichloroethane | x | x |  |
| Trichloroethylene | x | x |  |
| para-Dichlorobenzene | x | x |  |
| 1,1-Dichloroethylene | x | x |  |
| 1,1,1-Trichloroethane | x | x |  |
| Vinyl chloride | x |  |  |
| cis-1,2-Dichloroethylene | x | x |  |
| 1,2-Dichloropropane | x | x |  |
| Ethylbenzene | x | x |  |
| Monochlorobenzene | x | x |  |
| o-Dichlorobenzene | x | x |  |
| Styrene | x | x |  |
| Tetrachloroethylene | x | x |  |
| Toluene | x | x |  |
| trans-1,2-Dichloroethylene | x | x |  |
| Xylenes (total) | x | x |  |
| Alachlor |  | x |  |
| Aldicarb |  | x |  |
| Aldicarb sulfoxide |  | x |  |
| Aldicarb sulfone |  | x |  |
| Atrazine |  | x |  |
| Carbofuran |  | x |  |
| Chlordane |  | x |  |
| Dibromochloropropane | x | x |  |
| 2,4-D |  | x |  |
| Ethylene dibromide | x | x |  |
| Heptachlor |  | x |  |
| Heptachlor epoxide |  | x |  |

(Continued)

| Contaminant | Best Available Technologies |
| --- | --- |
|  | PTA1 | GAC2 | OX3 |
| Lindane |  | x |  |
| Methoxychlor |  | x |  |
| PCBs |  | x |  |
| Pentachlorophenol |  | x |  |
| Toxaphene |  | x |  |
| 2,4,5-TP |  | x |  |
| Benzo(a)pyrene |  | x |  |
| Dalapon |  | x |  |
| Dichloromethane | x |  |  |
| Di(2-ethylhexyl)adipate | x | x |  |
| Di(2-ethylhexyl)phthalate |  | x |  |
| Dinsoeb |  | x |  |
| Diquat |  | x |  |
| Endothal |  | x |  |
| Endrin |  | x |  |
| Glyphosate |  |  | x |
| Hexachlorobenzene |  | x |  |
| Hexachlorocyclopentadiene | x | x |  |
| Oxamyl (Vydate) |  | x |  |
| Picloram |  | x |  |
| Simazine |  | x |  |
| 1,2,4-Trichlorobenzene | x | x |  |
| 1,1,2-Trichloroethane | x | x |  |
| 2,3,7,8-TCDD (Dioxin) |  | x |  |
| TTHMs | [x] | x4 |  |
| HAAs |  | x4 |  |

1Packed Tower Aeration

2Granular Activated Carbon

3Oxidation (Chlorination or Ozonation)

4GAC10, as defined in section 5-1.1.  The other best available technology for TTHM and HAA MCL compliance is enhanced coagulation for TTHM and HAA precursor removal, as described in section 5-1.60.